## Slide 1
Equipment Efficiency Analysis
Chelmsford, UK

## Slide 2
Validation & Prediction
UK Chelmsford Office Validation Study
Currently using equipment installed in 2006
Performance Comparison with 2011 Equipment
City Multi R2 system vs a fancoil system with heat recovery
Green BIM & Sustainable Design

## Slide 3
Purpose built office
5 City Multi R2 Outdoor units and 25 indoor units
2 Lossnay heat recovery units providing fresh air
Monitored consumption data for an annual period
Existing Building
Green BIM & Sustainable Design

## Slide 4
Ground Floor
Systems: Olive and Yellow
Mitsubishi Lossnay Fresh Air Heat Recovery Unit
System Layout

## Slide 5
First Floor
Systems: Magenta, Blue, Green
Mitsubishi Lossnay Fresh Air Heat Recovery Unit
System Layout

## Slide 6
Building Simulation Inputs
Weather Data (London)
Calendar of occupation
Internal Conditions
  Infiltration
  Occupancy Gain
  Equipment Gain
  Fresh Air Requirement
Construction details

## Slide 7
HVAC Simulation Inputs
Air Side Schematic
Plant Side Schematic

## Slide 8
Manufacturer Data Import
Dedicated import function brings manufacturer data into Tas
Tas matches sized systems components to manufacturer-specific equipment
Exchanges system component data with manufacturer-level detail for accurate simulation

## Slide 9
Building Simulation Results
Hourly Building Demand
First Floor - Sensible Load - Day 50, Hour 12
First Floor – Hourly Sensible Load Results
3D Results Visualisation

## Slide 10
Mitsubishi Lossnay Heat Recovery:
Usage Hours

## Slide 11
Measured Consumption
Simulated Consumption (installed equipment)
HVAC System Consumption Comparison:
2006 Equipment

## Slide 12
Summary & Conclusion
Summary:
The 2011 equipment shows a 34.6% improvement on simulation of the installed 2006 equipment.
 | Annual Consumption (kWh) | Annual Cost (£) | Improvement (%)
Installed Equipment: Measured (2006) | 46,821 | 3,277 | -
Installed Equipment: Simulated (2006) | 42,494 | 2,982 | -
Replacement Equipment: Simulated (2011) | 27,810 | 1,947 | 34.6%
Conclusion:
Detailed simulation of building and plant leads to simulation consumption figures indicative of those seen in the real world application.
‘Good enough’ qualitative agreement between the predicted & measured data to make sound future predictions
Chart: 
| Measured (2006) | Simulated (2006) | Simulated (2011)
Annual Cost (£) | 3277 | 2982 | 1947