## Sheet1
ANNUAL HEATING LOADS
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas |  |  | Within
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX | Range
CASE | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 4.872 | 5.362 | 5.119 | 4.296 | 5.709 | YES
610 | 4.355 | 4.806 | 5.786 | 5.28 | 5.62 | 4.971 | 4.97 | 5.383 | 5.158 | 4.355 | 5.786 | YES
620 | 4.613 | 5.049 | 5.944 | 5.554 | 5.734 | 5.564 | 5.073 | 5.728 | 5.45 | 4.613 | 5.944 | YES
630 | 5.05 | 5.359 | 6.469 | 5.883 | 6.001 | 6.095 | 5.624 |  | 5.773 | 5.05 | 6.469 | YES
640 | 2.751 | 2.888 | 3.543 | 3.255 | 3.803 | 3.065 | 3.043 | 3.309 | 3.256 | 2.751 | 3.803 | YES
650 | 0 | 0 | 0 | 0 | 0 | 0 | 4.171e-06 | 0 | 0 | 0 | 4.171e-06 | YES
900 | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 1.655 | 2.041 | 1.803 | 1.17 | 2.041 | YES
910 | 1.575 | 1.862 | 2.254 | 2.174 | 2.282 | 2.063 | 2.097 | 2.22 | 2.088 | 1.575 | 2.282 | YES
920 | 3.313 | 3.752 | 4.255 | 4.093 | 4.058 | 4.235 | 3.776 | 4.3 | 4.076 | 3.313 | 4.3 | YES
930 | 4.143 | 4.347 | 5.335 | 4.755 | 4.728 | 5.168 | 4.74 |  | 4.715 | 4.143 | 5.335 | YES
940 | 0.793 | 1.021 | 1.239 | 1.231 | 1.411 | 1.179 | 1.08 | 1.323 | 1.244 | 0.793 | 1.411 | YES
950 | 0 | 0 | 0 | 0 | 0 | 0 | 7.801e-06 | 0 | 0 | 0 | 7.801e-06 | YES
960 | 2.311 | 2.664 | 2.928 | 2.884 | 2.851 | 2.943 | 3.373 | 2.816 | 2.907 | 2.311 | 3.373 | YES
195 | 4.167 | [7 empty] | 4.824 | 4.167 | 4.167
200 | 5.252 | [7 empty] | 5.752 | 5.252 | 5.252
210 | 6.456 | 6.559 |  |  |  |  | 6.554 | 6.967 | 7.066 | 6.456 | 6.967
215 | 5.547 | [7 empty] | 6.042 | 5.547 | 5.547
220 | 6.944 | 7.215 | 8.787 | 8.102 | 8.127 | 7.422 | 7.297 | 7.437 | 7.868 | 6.944 | 8.787 | YES
230 | 10.376 | 10.74 | 12.243 | 11.633 | 11.649 | 11.037 | 10.84 | 10.964 | 11.44 | 10.376 | 12.243 | YES
240 | 5.649 | 6.009 | 7.448 | 6.769 | 6.786 | 6.194 | 6.076 | 6.234 | 6.591 | 5.649 | 7.448 | YES
250 | 4.751 | 5.739 | 7.024 | 6.608 | 6.653 | 5.974 | 5.764 | 5.738 | 6.311 | 4.751 | 7.024 | YES
270 | 4.51 | 4.93 |  | 5.341 | 5.92 |  | 5.047 | 5.489 | 5.342 | 4.51 | 5.92 | YES
280 | 4.675 | 5.125 |  | 5.937 | 6.148 |  | 5.279 | 5.841 | 5.631 | 4.675 | 6.148 | YES
290 | 4.577 | 4.959 |  | 5.406 | 5.942 |  | 5.132 | 5.509 | 5.379 | 4.577 | 5.942 | YES
300 | 4.761 | 5.077 |  | 5.587 | 5.964 |  | 5.124 | 5.786 | 5.556 | 4.761 | 5.964 | YES
310 | 5.221 | 5.327 |  | 5.85 | 6.165 |  | 5.61 |  | 5.726 | 5.221 | 6.165 | YES
320 | 3.859 | 4.209 |  | 4.627 | 5.141 |  | 4.348 | 4.84 | 4.58 | 3.859 | 5.141 | YES
395 | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.855 | 4.839 | 5.204 | 4.799 | 5.835 | YES
400 | 6.9 | 7.075 | 8.77 | 7.966 | 7.973 | 7.287 | 7.166 | 7.326 | 7.745 | 6.9 | 8.77 | YES
410 | 8.596 | 8.873 | 10.506 | 9.726 | 9.734 | 9.019 | 8.936 | 9.085 | 9.524 | 8.596 | 10.506 | YES
420 | 7.298 | 7.61 | 9.151 | 8.365 | 8.373 | 7.774 | 7.697 | 7.863 | 8.233 | 7.298 | 9.151 | YES
430 | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.5 | 6.51 | 7.062 | 5.429 | 7.827 | YES
440 | 4.449 | 4.987 |  | 5.652 | 5.811 |  | 5.098 | 5.642 | 5.384 | 4.449 | 5.811 | YES
800 | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.94 | 5.861 | 6.558 | 4.868 | 7.228 | YES
810 | 1.839 | 2.446 |  | 3.004 | 2.828 |  | 2.567 | 2.962 | 2.801 | 1.839 | 3.004 | YES
ANNUAL COOLING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas |  |  | Within
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX | Range
CASE# | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.492 | 6.778 | 6.362 | 6.137 | 7.964 | YES
610 | 3.915 | 4.851 | 4.852 | 5.448 | 5.778 | 4.764 | 4.601 | 5.506 | 4.635 | 3.915 | 5.778 | YES
620 | 3.417 | 4.092 | 4.334 | 4.633 | 5.004 | 4.011 | 3.901 | 4.351 | 3.705 | 3.417 | 5.004 | YES
630 | 2.129 | 3.108 | 2.489 | 3.493 | 3.701 | 2.489 | 2.416 |  | 2.747 | 2.129 | 3.701 | YES
640 | 5.952 | 6.183 | 6.759 | 7.026 | 7.811 | 6.247 | 6.246 | 6.508 | 6.118 | 5.952 | 7.811 | YES
650 | 4.816 | 5.14 | 5.795 | 5.894 | 6.545 | 5.088 | 5.119 | 5.456 | 4.986 | 4.816 | 6.545 | YES
900 | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.485 | 2.599 | 2.326 | 2.132 | 3.415 | YES
910 | 0.821 | 1.533 | 0.976 | 1.872 | 1.854 | 1.428 | 1.326 | 1.767 | 1.196 | 0.821 | 1.872 | YES
920 | 1.84 | 2.616 | 2.44 | 2.943 | 3.092 | 2.457 | 2.418 | 2.613 | 2.135 | 1.84 | 3.092 | YES
930 | 1.039 | 1.934 | 1.266 | 2.173 | 2.238 | 1.439 | 1.416 |  | 1.531 | 1.039 | 2.238 | YES
940 | 2.079 | 2.536 | 2.34 | 3.036 | 3.241 | 2.489 | 2.383 | 2.516 | 2.25 | 2.079 | 3.241 | YES
950 | 0.387 | 0.526 | 0.538 | 0.921 | 0.589 | 0.551 | 0.5606 | 0.771 | 0.515 | 0.387 | 0.921 | YES
960 | 0.488 | 0.666 | 0.428 | 0.803 | 0.718 | 0.643 | 0.4113 | 0.786 | 0.563 | 0.4113 | 0.803 | YES
195 | 0.414 | [7 empty] | 0.471 | 0.414 | 0.414
200 | 0.57 | [7 empty] | 0.576 | 0.57 | 0.57
210 | 0.162 | 0.613 |  |  |  |  | 0.6679 | 0.641 | 0.475 | 0.162 | 0.6679
215 | 0.639 | [7 empty] | 0.603 | 0.639 | 0.639
220 | 0.186 | 0.701 | 0.399 | 0.827 | 0.835 | 0.734 | 0.7368 | 0.683 | 0.534 | 0.186 | 0.835 | YES
230 | 0.454 | 0.976 | 0.692 | 1.131 | 1.139 | 1.02 | 1.04 | 0.985 | 0.838 | 0.454 | 1.139 | YES
240 | 0.415 | 1.072 | 0.66 | 1.239 | 1.246 | 1.108 | 1.114 | 1.045 | 0.852 | 0.415 | 1.246 | YES
250 | 3.213 | 2.545 | 2.177 | 2.924 | 2.931 | 2.486 | 2.684 | 3.38 | 2.204 | 2.177 | 3.38 | YES
270 | 7.528 | 8.67 |  | 9.828 | 10.35 |  | 8.764 | 8.714 | 8.551 | 7.528 | 10.35 | YES
280 | 4.873 | 5.895 |  | 6.511 | 7.114 |  | 5.761 | 6.257 | 5.625 | 4.873 | 7.114 | YES
290 | 5.204 | 7.011 |  | 7.871 | 8.089 |  | 6.699 | 7.431 | 6.744 | 5.204 | 8.089 | YES
300 | 4.302 | 5.836 |  | 6.665 | 7.1 |  | 5.721 | 5.781 | 5.345 | 4.302 | 7.1 | YES
310 | 2.732 | 4.57 |  | 5.245 | 5.471 |  | 3.727 |  | 4.466 | 2.732 | 5.471 | YES
320 | 5.061 | 5.906 |  | 6.725 | 7.304 |  | 5.956 | 5.663 | 5.732 | 5.061 | 7.304 | YES
395 | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.01029 | 0.011 | 0.001 | 0 | 0.016 | YES
400 | 0 | 0.04 | 0.002 | 0.061 | 0.058 | 0.042 | 0.04468 | 0.044 | 0.009 | 0 | 0.061 | YES
410 | 0 | 0.059 | 0.01 | 0.084 | 0.084 | 0.063 | 0.06707 | 0.065 | 0.021 | 0 | 0.084 | YES
420 | 0.011 | 0.147 | 0.051 | 0.189 | 0.188 | 0.154 | 0.1575 | 0.143 | 0.078 | 0.011 | 0.189 | YES
430 | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.6174 | 0.875 | 0.43 | 0.422 | 0.875 | YES
440 | 3.967 | 4.172 |  | 4.674 | 5.204 |  | 3.975 | 4.684 | 3.949 | 3.967 | 5.204 | NO
800 | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.2073 | 0.325 | 0.095 | 0.055 | 0.325 | YES
810 | 1.052 | 1.405 |  | 1.711 | 1.708 |  | 1.191 | 1.624 | 1.149 | 1.052 | 1.711 | YES
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas |  |  | Within
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x |  |  | Range
CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX
600 | 3.437 | 3.94 | 4.045 | 4.258 |  | 4.037 | 3.9306 | 4.354 | 4.015 | 3.437 | 4.354 | YES
610 | 3.437 | 3.941 | 4.034 | 4.258 |  | 4.037 | 3.9222 | 4.354 | 4.015 | 3.437 | 4.354 | YES
620 | 3.591 | 3.941 | 4.046 | 4.277 |  | 4.277 | 3.9222 | 4.379 | 4.016 | 3.591 | 4.379 | YES
630 | 3.592 | 3.941 | 4.025 | 4.28 |  | 4.278 | 3.9222 |  | 4.016 | 3.592 | 4.28 | YES
640 | 5.232 | 5.486 | 5.943 | 6.53 |  | 6.347 | 5.7222 | 6.954 | 6.419 | 5.232 | 6.954 | YES
650 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | YES
900 | 2.85 | 3.453 | 3.557 | 3.76 |  | 3.608 | 3.5167 | 3.797 | 3.543 | 2.85 | 3.797 | YES
910 | 2.858 | 3.456 | 3.564 | 3.764 |  | 3.618 | 3.5361 | 3.801 | 3.546 | 2.858 | 3.801 | YES
920 | 3.308 | 3.703 | 3.805 | 4.013 |  | 4.029 | 3.7083 | 4.061 | 3.764 | 3.308 | 4.061 | YES
930 | 3.355 | 3.732 | 3.832 | 4.042 |  | 4.064 | 3.7444 |  | 3.793 | 3.355 | 4.064 | YES
940 | 3.98 | 5.028 | 5.665 | 6.116 |  | 6.117 | 5.1222 | 6.428 | 6.016 | 3.98 | 6.428 | YES
950 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | YES
960 | 2.41 | 2.751 | 2.727 | 2.863 |  | 2.852 | 2.522 | 2.779 | 2.776 | 2.41 | 2.863 | YES
195 | 2.004 | [7 empty] | 2.164 | 2.004 | 2.004
200 | 2.651 | [7 empty] | 2.601 | 2.651 | 2.651
210 | 2.701 | 2.973 |  |  |  |  | 2.9806 | 3.325 | 3.047 | 2.701 | 3.325
215 | 2.787 | [7 empty] | 2.742 | 2.787 | 2.787
220 | 2.867 | 3.28 | 3.465 | 3.695 |  | 3.348 | 3.3361 | 3.52 | 3.41 | 2.867 | 3.695 | YES
230 | 4.386 | 4.984 | 4.994 | 5.279 |  | 5.159 | 4.8917 | 5.107 | 4.979 | 4.386 | 5.279 | YES
240 | 2.685 | 3.1 | 3.282 | 3.495 |  | 3.159 | 3.1528 | 3.333 | 3.228 | 2.685 | 3.495 | YES
250 | 2.866 | 3.279 | 3.465 | 3.695 |  | 3.341 | 3.3361 | 3.525 | 3.41 | 2.866 | 3.695 | YES
270 | 2.863 | 3.277 |  | 3.661 |  |  | 3.3361 | 3.738 | 3.413 | 2.863 | 3.738 | YES
280 | 2.864 | 3.278 |  | 3.685 |  |  | 3.3361 | 3.759 | 3.413 | 2.864 | 3.759 | YES
290 | 2.863 | 3.277 |  | 3.661 |  |  | 3.3278 | 3.738 | 3.413 | 2.863 | 3.738 | YES
300 | 3.014 | 3.276 |  | 3.681 |  |  | 3.3278 | 3.77 | 3.413 | 3.014 | 3.77 | YES
310 | 3.015 | 3.277 |  | 3.669 |  |  | 3.3278 |  | 3.413 | 3.015 | 3.669 | YES
320 | 2.861 | 3.275 |  | 3.651 |  |  | 3.3361 | 3.735 | 3.412 | 2.861 | 3.735 | YES
395 | 2.062 | 2.209 | 2.328 | 2.385 |  | 2.263 | 2.2211 | 2.27 | 2.293 | 2.062 | 2.385 | YES
400 | 2.867 | 3.28 | 3.476 | 3.695 |  | 3.342 | 3.3361 | 3.52 | 3.41 | 2.867 | 3.695 | YES
410 | 3.625 | 4.124 | 4.233 | 4.487 |  | 4.227 | 4.1139 | 4.314 | 4.195 | 3.625 | 4.487 | YES
420 | 3.443 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.126 | 4.013 | 3.443 | 4.287 | YES
430 | 3.442 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.137 | 4.013 | 3.442 | 4.287 | YES
440 | 3.439 | 3.942 |  | 4.277 |  |  | 3.9306 | 4.376 | 4.015 | 3.439 | 4.376 | YES
800 | 3.227 | 3.793 | 3.909 | 4.138 |  | 3.902 | 3.7861 | 3.939 | 3.846 | 3.227 | 4.138 | YES
810 | 2.979 | 3.566 |  | 3.915 |  |  | 3.6056 | 3.963 | 3.646 | 2.979 | 3.963 | YES
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas |  |  | Within
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x |  |  | Range
CASE# | kW | kW | kW | kW | kW | kW | kW | kW | KW | MIN | MAX
600 | 6.194 | 5.965 | 6.656 | 6.827 |  | 6.286 | 6.4861 | 6.812 | 6.115 | 5.965 | 6.827 | YES
610 | 5.669 | 5.824 | 6.064 | 6.371 |  | 6.17 | 5.675 | 6.146 | 5.829 | 5.669 | 6.371 | YES
620 | 3.634 | 4.075 | 4.43 | 4.593 |  | 4.297 | 4.275 | 5.096 | 3.889 | 3.634 | 5.096 | YES
630 | 3.072 | 3.704 | 3.588 | 4.116 |  | 3.665 | 3.6083 |  | 3.442 | 3.072 | 4.116 | YES
640 | 6.161 | 5.892 | 6.576 | 6.776 |  | 6.25 | 6.4417 | 6.771 | 6.073 | 5.892 | 6.776 | YES
650 | 6.031 | 5.831 | 6.516 | 6.671 |  | 6.143 | 6.3778 | 6.679 | 5.958 | 5.831 | 6.679 | YES
900 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 3.114 | 2.888 | 3.871 | YES
910 | 1.896 | 2.5 | 2.336 | 3.277 |  | 2.786 | 2.7917 | 3.147 | 2.404 | 1.896 | 3.277 | YES
920 | 2.385 | 2.933 | 3.109 | 3.487 |  | 3.071 | 3.05 | 3.505 | 2.769 | 2.385 | 3.505 | YES
930 | 1.873 | 2.546 | 2.388 | 3.08 |  | 2.486 | 2.4983 |  | 2.404 | 1.873 | 3.08 | YES
940 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 3.114 | 2.888 | 3.871 | YES
950 | 2.033 | 2.621 | 2.664 | 3.17 |  | 2.677 | 2.6861 | 2.867 | 2.527 | 2.033 | 3.17 | YES
960 | 0.953 | 1.144 | 1.057 | 1.37 |  | 1.179 | 1.378 | 1.403 | 1.116 | 0.953 | 1.403 | YES
195 | kW: 0.651; KW: 0.777; MIN: 0.651; MAX: 0.651
200 | kW: 0.863; KW: 0.93; MIN: 0.863; MAX: 0.863
210 | 0.476 | 1.017 |  |  |  |  | 1.0678 | 1.142 | 0.944 | 0.476 | 1.142
215 | kW: 1.007; KW: 0.978; MIN: 1.007; MAX: 1.007
220 | 0.56 | 1.166 | 0.937 | 1.34 |  | 1.215 | 1.1789 | 1.213 | 1.059 | 0.56 | 1.34 | YES
230 | 1.059 | 1.646 | 1.455 | 1.875 |  | 1.7 | 1.7078 | 1.749 | 1.581 | 1.059 | 1.875 | YES
240 | 0.739 | 1.347 | 1.119 | 1.54 |  | 1.398 | 1.3614 | 1.397 | 1.241 | 0.739 | 1.54 | YES
250 | 3.36 | 3.036 | 2.605 | 2.59 |  | 2.258 | 3.2278 | 4.912 | 2.73 | 2.258 | 4.912 | YES
270 | 6.356 | 6.641 |  | 7.234 |  |  | 6.7639 | 6.867 | 6.528 | 6.356 | 7.234 | YES
280 | 4.444 | 4.631 |  | 5.22 |  |  | 4.7861 | 5.236 | 4.514 | 4.444 | 5.236 | YES
290 | 6.269 | 6.555 |  | 6.976 |  |  | 6.2028 | 6.621 | 6.43 | 6.2028 | 6.976 | YES
300 | 3.404 | 4.093 |  | 4.657 |  |  | 4.2778 | 4.929 | 3.874 | 3.404 | 4.929 | YES
310 | 2.848 | 3.749 |  | 4.164 |  |  | 3.5889 |  | 3.467 | 2.848 | 4.164 | YES
320 | 5.701 | 5.946 |  | 6.553 |  |  | 6.1778 | 6.141 | 5.893 | 5.701 | 6.553 | YES
395 | 0 | 0.362 | 0 | 0.394 |  | 0.356 | 0.3625 | 0.345 | 0.19 | 0 | 0.394 | YES
400 | 0 | 0.581 | 0.265 | 0.666 |  | 0.612 | 0.61333 | 0.572 | 0.422 | 0 | 0.666 | YES
410 | 0.035 | 0.699 | 0.413 | 0.814 |  | 0.724 | 0.74306 | 0.71 | 0.563 | 0.035 | 0.814 | YES
420 | 0.258 | 0.923 | 0.631 | 1.047 |  | 0.938 | 0.93778 | 0.921 | 0.783 | 0.258 | 1.047 | YES
430 | 1.493 | 1.772 | 1.427 | 1.762 |  | 1.575 | 1.7983 | 2.578 | 1.485 | 1.427 | 2.578 | YES
440 | 4.546 | 4.424 |  | 5.053 |  |  | 4.6861 | 5.278 | 4.449 | 4.424 | 5.278 | YES
800 | 0.585 | 0.967 | 0.743 | 1.352 |  | 1.028 | 0.98278 | 1.358 | 0.845 | 0.585 | 1.358 | YES
810 | 1.852 | 2.357 |  | 2.991 |  |  | 2.3436 | 2.862 | 2.289 | 1.852 | 2.991 | YES
FREE-FLOAT TEMPERATURE OUTPUT
MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas |  |  | Within
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x |  |  | Range
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | MIN | MAX
600FF | 64.929 | 65.11 | 69.5 | 68.6 |  | 64.9 | 65.25 | 65.25 | 64.029 | 64.9 | 69.5 | NO
900FF | 41.812 | 43.44 | 42.7 | 44.8 |  | 43 | 42.46 | 43.17 | 41.92 | 41.812 | 44.8 | YES
650FF | 63.236 | 63.45 | 68.2 | 67 |  | 63.3 | 63.74 | 63.82 | 62.526 | 63.236 | 68.2 | NO
950FF | 35.54 | 36.23 | 35.9 | 38.5 |  | 36.1 | 35.67 | 37.58 | 35.636 | 35.54 | 38.5 | YES
960 | 48.943 | 48.88 | 49 | 51 |  | 50.2 | 55.34 | 48.92 | 48.559 | 48.88 | 55.34 | NO
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas |  |  | Within
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x |  |  | Range
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | MIN | MAX
600FF | -15.565 | -17.05 | -18.8 | -18 |  | -17.8 | -17.81 | -18.47 | -18.854 | -18.8 | -15.565 | NO
900FF | -1.647 | -3.15 | -4.3 | -4.5 |  | -4 | -6.38 | -5.64 | -4.354 | -6.38 | -1.647 | YES
650FF | -22.564 | -22.96 | -21.6 | -23 |  | -22.9 | -22.83 | -22.91 | -23.025 | -23 | -21.6 | NO
950FF | -19.484 | -20.04 | -18.6 | -19.7 |  | -20.2 | -19.34 | -19.96 | -19.954 | -20.2 | -18.6 | YES
960 | 2.729 | 1.63 | 3.9 | 3.1 |  | 1.4 | -2.82 | -0.39 | 0.938 | -2.82 | 3.9 | YES
AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas |  |  | Within
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x |  |  | Range
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | MIN | MAX
600FF | 25.126 | 25.43 | 24.6 | 25.48 | 25.93 | 25.2 | 24.49 | 24.22 | 24.585 | 24.22 | 25.93 | YES
900FF | 25.453 | 25.93 | 24.7 | 25.49 | 25.72 | 25.2 | 24.47 | 24.45 | 24.638 | 24.45 | 25.93 | YES
650FF | 18.234 | 18.69 | 19.1 | 18.96 | 19.62 | 18.4 | 17.99 | 18.36 | 18.101 | 17.99 | 19.62 | YES
950FF | 14.14 | 14.26 | 14.3 | 14.97 | 14.29 | 14 | 14.53 | 14.64 | 13.938 | 14 | 14.97 | NO
960 | 27.49 | 27.72 | 28 | 28.69 | 28.54 | 28 | 28.96 | 26.43 | 27.282 | 26.43 | 28.96 | YES
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
SURFACE | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
NORTH | 427 |  | 434 | 456 | 407.3 | 457 | 367.4 | 453 | 373.122
EAST | 959 |  | 1155 | 1083 | 1217.3 | 1082 | 1101 | 962 | 908.623
WEST | 1086 |  | 1079 | 1003 | 856.5 | 1002 | 1012 | 1090 | 1065.847
SOUTH | 1456 |  | 1566 | 1476 | 1467.7 | 1474 | 1522 | 1468 | 1451.302
HORZ. | 1797 |  | 1831 | 1832 | 1831.8 | 1832 | 1832 | 1832 | 1831.069
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
920WEST | 732 |  | 735 | 689 | 562.96 | 642 | 661.67 | 706 | 737.919
900SOUTH | 946 |  | 1051 | 962 | 954.3 | 926 | 984.17 | 914 | 1002.315
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
930WEST | 599 |  | 481 | 554 | 441.3 | 431 | 437.5 |  | 590.536
910SOUTH | 785 |  | 831 | 803 | 774.86 | 757 | 782 | 809 | 831.518
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1.6 |  | 1.5 | 3.0447 | 3.02 | 3 | 3.05 | 3 | 3
8 | 13.8 |  | 12.59 | 20.6464 | 20.59 | 21 | 20.69 | 20.68 | 20.4
9 | 31.6 |  | 30.01 | 38.8836 | 38.83 | 39 | 38.94 | 38.94 | 37.9
10 | 48.3 |  | 46.23 | 54.5664 | 54.53 | 55 | 54.67 | 54.56 | 53.5
11 | 61.6 |  | 59.31 | 65.9733 | 54.77 | 66 | 66.08 | 65.99 | 66.527
12 | 69.3 |  | 65.05 | 71.7839 | 59.65 | 72 | 71.92 | 71.74 | 71.884
13 | 71.7 |  | 66.98 | 72.2839 | 60.1 | 72 | 72.42 | 72.3 | 72.476
14 | 68.1 |  | 63.11 | 66.4075 | 55.24 | 66 | 66.53 | 66.38 | 66.502
15 | 58.9 |  | 51.79 | 54.8997 | 45.68 | 55 | 55 | 54.8 | 53.5
16 | 44.4 |  | 37.13 | 38.8836 | 32.37 | 39 | 38.94 | 38.84 | 37.9
17 | 26.9 |  | 19.14 | 20.4797 | 17.06 | 20 | 20.52 | 20.46 | 19.9
18 | 8.7 |  | 4.62 | 3.0447 | 2.54 | 3 | 3.05 | 0 | 3
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1.6 |  | 1.8 | 2.9967 | 3 | 3 | 2.99 | 3 | 3
8 | 13.5 |  | 13.92 | 20.1831 | 20.24 | 20 | 20.17 | 20.15 | 20.4
9 | 31 |  | 31.75 | 37.955 | 38.01 | 38 | 37.92 | 37.9 | 37.812
10 | 47.1 |  | 45.24 | 53.2444 | 53.27 | 53 | 53.17 | 53.15 | 53.425
11 | 59.7 |  | 56.63 | 64.4672 | 53.37 | 64 | 64.39 | 64.4 | 64.291
12 | 67.4 |  | 61.58 | 69.9819 | 57.91 | 70 | 69.89 | 69.95 | 69.751
13 | 70.1 |  | 63.7 | 70.8061 | 58.3 | 71 | 70.75 | 71.16 | 70.629
14 | 67.3 |  | 61.46 | 65.6633 | 54.15 | 66 | 65.69 | 66.02 | 65.424
15 | 58.9 |  | 51.67 | 54.9214 | 45.38 | 55 | 55.03 | 55.16 | 53.5
16 | 44.9 |  | 37.2 | 39.4869 | 32.7 | 40 | 39.61 | 39.73 | 37.9
17 | 27.6 |  | 16.72 | 21.2906 | 17.7 | 21 | 21.42 | 21.6 | 19.9
18 | 9 |  | 2.52 | 3.27 | 2.73 | 3 | 3.28 | 0 | 3
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.5 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 0
6 | 17.9 |  | 20.11 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 30.6
7 | 58.6 |  | 70.22 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 94.506
8 | 100.4 |  | 108.13 | 99.9892 | 112.85 | 104 | 71.22 | 107.47 | 134.229
9 | 205.9 |  | 219.58 | 211.0064 | 164.86 | 217 | 187.72 | 232.33 | 224.166
10 | 326 |  | 343.67 | 331.0058 | 291.84 | 336 | 314.17 | 349.16 | 335.319
11 | 415.1 |  | 435.54 | 418.1717 | 389.26 | 423 | 404.44 | 430.22 | 417.397
12 | 454.8 |  | 475.37 | 454.9942 | 437.2 | 459 | 443.61 | 459.85 | 452.118
13 | 455.6 |  | 488.49 | 464.5689 | 455.75 | 469 | 452.5 | 462.28 | 460.546
14 | 408.6 |  | 443.66 | 413.6364 | 413.67 | 418 | 400.56 | 404.57 | 408.185
15 | 321.2 |  | 367.07 | 334.2839 | 341.53 | 340 | 316.94 | 319.26 | 325.077
16 | 200.6 |  | 246.71 | 211.9439 | 223.71 | 218 | 188.89 | 193.61 | 195.727
17 | 102.3 |  | 119.19 | 111.7408 | 105.72 | 115 | 86.03 | 132.3 | 88.56
18 | 78.8 |  | 68.86 | 73.0792 | 68.47 | 74 | 69.78 | 76.6 | 68.496
19 | 37.1 |  | 19.75 | 17.7025 | 14.35 | 18 | 17.61 | 18.05 | 16.936
20 | 1.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.4 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 0
6 | 17.9 |  | 19.96 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 30.6
7 | 58.5 |  | 65.86 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 89.532
8 | 91.8 |  | 97.11 | 99.9892 | 112.85 | 104 | 71.22 | 72 | 109.827
9 | 113.7 |  | 116.89 | 120.0506 | 121.41 | 125 | 85.58 | 92.6 | 113.158
10 | 131.2 |  | 128.97 | 134.9631 | 123.51 | 140 | 98.03 | 112.8 | 109.184
11 | 145.7 |  | 138.05 | 149.5847 | 125.06 | 154 | 109.14 | 136.75 | 113.44
12 | 153.8 |  | 141.34 | 153.1336 | 121.07 | 157 | 113.06 | 150.9 | 131.17
13 | 267.7 |  | 243.51 | 266.4489 | 117.94 | 270 | 235.17 | 382.5 | 240.093
14 | 464.8 |  | 462.83 | 461.2772 | 333.68 | 463 | 453.89 | 576.81 | 432.732
15 | 635.1 |  | 664.62 | 635.5103 | 525.35 | 635 | 652.5 | 744.52 | 619.037
16 | 738.3 |  | 786.35 | 719.3256 | 634.59 | 715 | 762.78 | 807.29 | 730.828
17 | 623.9 |  | 649.05 | 502.7889 | 478.44 | 497 | 568.33 | 541.68 | 536.463
18 | 296.9 |  | 243.11 | 141.2425 | 140.3 | 139 | 158 | 145.25 | 154.647
19 | 68.8 |  | 43.19 | 25.2472 | 21.96 | 24 | 26.6 | 24.9 | 30.707
20 | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOURLY FREE FLOAT TEMPERATURE 9.1.x
CASE 600FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
1 | -8.88 | -12.0409 | -12.3 | -12.21 |  | -12.1 | -12.02 | -13.04 | -11.949
2 | -10.48 | -13.523 | -14.1 | -13.8 |  | -13.7 | -13.5 | -14.59 | -13.658
3 | -11.76 | -14.4018 | -15.4 | -14.9 |  | -14.7 | -14.7 | -15.65 | -14.937
4 | -12.75 | -15.2598 | -16.3 | -15.79 |  | -15.6 | -15.65 | -16.46 | -16.005
5 | -13.69 | -15.9988 | -17.1 | -16.55 |  | -16.4 | -16.47 | -17.16 | -16.892
6 | -14.49 | -16.3983 | -17.9 | -17.2 |  | -17 | -17.14 | -17.79 | -17.66
7 | -15.15 | -17.0108 | -18.5 | -17.74 |  | -17.6 | -17.7 | -18.32 | -18.31
8 | -15.63 | -17.0531 | -18.8 | -17.85 |  | -17.8 | -17.59 | -18.47 | -18.854
9 | -14.63 | -13.7364 | -14.7 | -14.88 |  | -14.6 | -13.46 | -15.47 | -16.743
10 | -10.03 | -7.9937 | -7.8 | -9.07 |  | -8.9 | -7.099 | -9.56 | -11.782
11 | -2.2 | 2.6043 | 3.2 | 1.01 |  | 1 | 3.657 | 0.49 | -2.343
12 | 8.84 | 12.2151 | 13.4 | 11.21 |  | 10.7 | 13.49 | 10.39 | 7.05
13 | 18.96 | 20.8602 | 22.3 | 20.03 |  | 19.2 | 21.77 | 18.75 | 15.981
14 | 27.19 | 27.532 | 29.5 | 27.27 |  | 26.1 | 28.26 | 25.48 | 23.712
15 | 33.22 | 31.3289 | 33.8 | 31.34 |  | 29.8 | 32.09 | 29.21 | 29.21
16 | 35.51 | 31.0594 | 33.5 | 31.47 |  | 29.7 | 32.16 | 28.97 | 30.883
17 | 31.46 | 24.2801 | 27 | 25.96 |  | 23.9 | 25.71 | 22.58 | 24.305
18 | 23.99 | 17.4634 | 19.7 | 18.96 |  | 17.6 | 18.84 | 15.59 | 17.809
19 | 18.08 | 12.0529 | 13.7 | 13.04 |  | 12.2 | 13.1 | 10.2 | 12.365
20 | 13.02 | 7.5727 | 8.7 | 8.31 |  | 7.8 | 8.408 | 6.02 | 7.798
21 | 8.87 | 3.5981 | 4.4 | 4.27 |  | 4 | 4.387 | 2.39 | 3.85
22 | 5.12 | 0.51861 | 1 | 0.99 |  | 0.9 | 0.9659 | -0.59 | 0.619
23 | 2.03 | -1.9381 | -1.9 | -1.66 |  | -1.7 | -1.781 | -3.04 | -2.035
24 | -1.03 | -4.0741 | -4.4 | -3.92 |  | -3.9 | -4.032 | -5.14 | -4.386
HOURLY FREE FLOAT TEMPERATURE 9.1.x
CASE 900FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
1 | 1.61 | -0.17002 | -0.9 | -1.31 |  | -0.7 | -3.455 | -2.68 | -0.898
2 | 0.93 | -0.79333 | -1.6 | -1.97 |  | -1.4 | -3.986 | -3.33 | -1.549
3 | 0.49 | -1.0908 | -2 | -2.37 |  | -1.8 | -4.395 | -3.72 | -2.011
4 | 0.07 | -1.6745 | -2.5 | -2.81 |  | -2.3 | -4.8 | -4.1 | -2.528
5 | -0.41 | -2.0414 | -2.9 | -3.25 |  | -2.7 | -5.216 | -4.51 | -3.017
6 | -0.87 | -2.4328 | -3.4 | -3.68 |  | -3.2 | -5.604 | -4.93 | -3.481
7 | -1.27 | -2.9702 | -3.9 | -4.1 |  | -3.6 | -5.984 | -5.34 | -3.945
8 | -1.64 | -3.1541 | -4.3 | -4.4 |  | -4 | -6.078 | -5.64 | -4.354
9 | -1.54 | -2.3938 | -3.3 | -3.45 |  | -3.2 | -4.717 | -4.59 | -3.891
10 | -0.4 | -1.0924 | -1.6 | -1.6 |  | -1.7 | -2.977 | -2.64 | -2.605
11 | 1.59 | 1.5953 | 1.2 | 1.66 |  | 0.9 | 0.2494 | 0.75 | 0.017
12 | 4.4 | 3.6249 | 3.5 | 4.4 |  | 3.1 | 2.539 | 3.26 | 2.193
13 | 6.72 | 5.6203 | 5.5 | 6.56 |  | 5.1 | 4.382 | 4.99 | 4.267
14 | 8.66 | 7.3237 | 7.2 | 8.39 |  | 6.8 | 5.853 | 6.51 | 6.131
15 | 10.02 | 8.2691 | 8 | 9.04 |  | 7.6 | 6.614 | 7.11 | 7.324
16 | 10.4 | 8.1513 | 7.9 | 8.58 |  | 7.4 | 6.333 | 6.68 | 7.542
17 | 9.41 | 6.5309 | 6.2 | 6.44 |  | 5.8 | 4.204 | 4.24 | 5.425
18 | 7.66 | 5.2506 | 4.7 | 4.43 |  | 4.4 | 2.869 | 2.45 | 4.051
19 | 6.74 | 4.5191 | 3.8 | 3.37 |  | 3.6 | 2.107 | 1.71 | 3.237
20 | 6 | 3.8832 | 3.2 | 2.73 |  | 3 | 1.581 | 1.32 | 2.617
21 | 5.41 | 3.2206 | 2.7 | 2.11 |  | 2.4 | 1.047 | 0.82 | 2
22 | 4.74 | 2.8485 | 2.2 | 1.66 |  | 1.9 | 0.5504 | 0.42 | 1.497
23 | 4.2 | 2.4745 | 1.7 | 1.26 |  | 1.5 | 0.1517 | 0.05 | 1.059
24 | 3.66 | 1.8994 | 1.2 | 0.83 |  | 1 | -0.238 | -0.34 | 0.562
HOURLY FREE FLOAT TEMPERATURE 9.1.x
CASE 650FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
1 | 22.58 | 22.223 | 21.8 | 22.37 |  | 22.4 | 22.69 | 22.26 | 22.052
2 | 21.15 | 21.1546 | 20.8 | 21.19 |  | 21.2 | 21.33 | 21.11 | 20.905
3 | 20.23 | 20.3068 | 19.9 | 20.33 |  | 20.4 | 20.41 | 20.28 | 20.023
4 | 19.45 | 19.5218 | 19.1 | 19.54 |  | 19.5 | 19.61 | 19.49 | 19.207
5 | 18.95 | 19.295 | 18.8 | 19.21 |  | 19.2 | 19.16 | 19.14 | 18.838
6 | 19.24 | 19.9144 | 19.5 | 19.86 |  | 19.9 | 19.6 | 19.81 | 19.55
7 | 21.16 | 22.5284 | 22.2 | 22.51 |  | 22.5 | 21.68 | 22.49 | 22.32
8 | 23.56 | 25.0275 | 24 | 24.89 |  | 24.7 | 23.47 | 24.81 | 24.738
9 | 25.67 | 28.3327 | 27.3 | 28.29 |  | 27.9 | 26.38 | 28.04 | 28.203
10 | 28.91 | 31.8311 | 31.5 | 32.42 |  | 31.7 | 30.35 | 32.11 | 32.235
11 | 32.8 | 35.825 | 36.2 | 37.12 |  | 36.2 | 34.82 | 36.54 | 36.725
12 | 37.49 | 40.1973 | 41.1 | 42.08 |  | 40.8 | 39.38 | 41.15 | 41.432
13 | 41.94 | 43.9026 | 45.4 | 46.46 |  | 45 | 43.48 | 45.03 | 45.452
14 | 45.43 | 46.3464 | 48.4 | 49.69 |  | 48.1 | 46.14 | 47.65 | 48.323
15 | 47.41 | 47.6362 | 50.1 | 51.3 |  | 49.6 | 47.4 | 49.04 | 49.811
16 | 47.84 | 47.6029 | 50.1 | 51.28 |  | 49.7 | 47.33 | 49.28 | 49.598
17 | 47.01 | 47.3406 | 49.1 | 50.46 |  | 49.1 | 46.71 | 48.73 | 48.628
18 | 45.53 | 45.3964 | 46.8 | 48.37 |  | 47.2 | 45.28 | 46.58 | 46.648
19 | 37.37 | 33.7034 | 34 | 35.39 |  | 35.1 | 33.1 | 34.91 | 34.677
20 | 31.57 | 30.8664 | 30.9 | 31.63 |  | 31.6 | 30.49 | 30.69 | 31.294
21 | 29.05 | 28.695 | 28.5 | 29.12 |  | 29.2 | 28.55 | 28.81 | 28.956
22 | 26.92 | 26.4968 | 26.3 | 26.83 |  | 26.9 | 26.66 | 26.66 | 26.677
23 | 25.52 | 25.6844 | 25.4 | 25.87 |  | 25.9 | 25.55 | 25.69 | 25.704
24 | 23.84 | 24.0543 | 23.7 | 24.19 |  | 24.2 | 24.26 | 24.1 | 23.988
HOURLY FREE FLOAT TEMPERATURE 9.1.x
CASE 950FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
1 | 24.36 | 24.5601 | 24.2 | 24.52 |  | 24.6 | 25.28 | 24.53 | 24.245
2 | 23.46 | 23.8963 | 23.5 | 23.81 |  | 23.9 | 24.47 | 23.8 | 23.56
3 | 22.86 | 23.3126 | 22.9 | 23.22 |  | 23.3 | 23.87 | 23.23 | 22.967
4 | 22.27 | 22.6823 | 22.3 | 22.6 |  | 22.7 | 23.26 | 22.6 | 22.333
5 | 21.86 | 22.4527 | 22 | 22.32 |  | 22.4 | 22.87 | 22.27 | 22.029
6 | 22.01 | 22.8128 | 22.5 | 22.77 |  | 22.8 | 23.06 | 22.67 | 22.463
7 | 23.32 | 24.6678 | 24.3 | 24.73 |  | 24.6 | 24.38 | 24.55 | 24.38
8 | 25.62 | 27.3586 | 26.5 | 27.59 |  | 27.1 | 27.21 | 27.57 | 26.806
9 | 27.59 | 28.3229 | 27.5 | 29.09 |  | 28.2 | 27.98 | 29.42 | 28.004
10 | 28.82 | 29.2074 | 28.6 | 30.5 |  | 29.3 | 29.11 | 30.68 | 29.15
11 | 29.84 | 30.1901 | 29.8 | 31.98 |  | 30.5 | 30.31 | 31.91 | 30.363
12 | 30.98 | 31.3352 | 31.1 | 33.56 |  | 31.7 | 31.53 | 33.27 | 31.686
13 | 32.08 | 32.1879 | 32.2 | 34.79 |  | 32.8 | 32.55 | 34.27 | 32.76
14 | 32.85 | 32.845 | 33 | 35.65 |  | 33.6 | 33.15 | 34.9 | 33.54
15 | 33.33 | 33.1198 | 33.4 | 35.96 |  | 34 | 33.37 | 35.19 | 33.945
16 | 33.55 | 33.2478 | 33.5 | 35.82 |  | 34.1 | 33.38 | 35.28 | 33.927
17 | 33.44 | 33.3523 | 33.5 | 35.61 |  | 34.1 | 33.37 | 35.3 | 33.843
18 | 33.23 | 32.996 | 33.1 | 34.93 |  | 33.7 | 33.16 | 34.71 | 33.449
19 | 30.92 | 30.203 | 30 | 30.96 |  | 30.6 | 30.43 | 30.74 | 30.366
20 | 29.17 | 29.3534 | 29.1 | 29.79 |  | 29.6 | 29.61 | 29.38 | 29.371
21 | 28.31 | 28.5416 | 28.2 | 28.83 |  | 28.7 | 28.89 | 27.64 | 28.514
22 | 27.27 | 27.3759 | 27.1 | 27.59 |  | 27.5 | 27.93 | 27.46 | 27.325
23 | 26.62 | 27.174 | 26.8 | 27.28 |  | 27.3 | 27.42 | 27.1 | 27.029
24 | 25.54 | 25.9805 | 25.7 | 26.1 |  | 26.1 | 26.59 | 26.02 | 25.867
HOURLY HEATING & COOLING LOAD 9.1.x
CASE 600 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
1 | 3.25 | 3.8018 | 3.926 | 4.127 |  | 3.925 | 3.7667 | 4.225 | 3.86
2 | 3.409 | 3.9109 | 4.035 | 4.258 |  | 4.037 | 3.8667 | 4.354 | 3.981
3 | 3.392 | 3.8658 | 4.013 | 4.229 |  | 4.003 | 3.9028 | 4.321 | 3.962
4 | 3.381 | 3.9196 | 4.041 | 4.22 |  | 4.001 | 3.8944 | 4.308 | 4.004
5 | 3.417 | 3.9401 | 4.045 | 4.22 |  | 4.001 | 3.9167 | 4.303 | 4.015
6 | 3.432 | 3.9258 | 4.036 | 4.221 |  | 4.001 | 3.9306 | 4.307 | 4.005
7 | 3.421 | 3.937 | 4.045 | 4.222 |  | 4.001 | 3.9306 | 4.307 | 4.013
8 | 3.337 | 3.7023 | 3.857 | 4.09 |  | 3.898 | 3.7528 | 4.167 | 3.929
9 | 2.767 | 2.6752 | 2.559 | 2.902 |  | 2.706 | 2.4228 | 2.912 | 3.049
10 | 1.497 | 1.3833 | 0.843 | 1.275 |  | 1.151 | 0.79667 | 1.466 | 1.602
11 | 0.151 | 0 | 0 | 0 |  | 0 | -0.034833 | 0 | 0
12 | -0.771 | -1.2242 | -1.552 | -1.066 |  | -1.036 | -1.435 | -0.424 | -0.305
13 | -2.66 | -2.4871 | -2.854 | -2.586 |  | -2.498 | -2.7203 | -2.364 | -2.18
14 | -3.575 | -2.9579 | -3.398 | -3.225 |  | -3.085 | -3.1556 | -2.759 | -3.024
15 | -3.527 | -2.631 | -3.116 | -2.826 |  | -2.637 | -2.8444 | -2.431 | -3.082
16 | -2.435 | -1.3491 | -1.82 | -1.552 |  | -1.345 | -1.7158 | -1.14 | -2.105
17 | -0.356 | 0 | 0 | -0.001 |  | 0 | 0 | 0 | 0
18 | 0.243 | 0.95017 | 0.775 | 0.8 |  | 0.88 | 0.77306 | 1.292 | 0.779
19 | 1.53 | 2.3779 | 2.232 | 2.34 |  | 2.331 | 2.3014 | 2.445 | 2.301
20 | 2.321 | 2.8665 | 2.933 | 2.988 |  | 2.949 | 2.9667 | 2.941 | 2.956
21 | 2.641 | 3.2126 | 3.323 | 3.365 |  | 3.309 | 3.2778 | 3.405 | 3.322
22 | 2.899 | 3.2845 | 3.487 | 3.532 |  | 3.347 | 3.4611 | 3.594 | 3.467
23 | 3.017 | 3.3307 | 3.514 | 3.605 |  | 3.494 | 3.5 | 3.696 | 3.484
24 | 3.008 | 3.388 | 3.561 | 3.663 |  | 3.527 | 3.4722 | 3.769 | 3.533
HOURLY HEATING & COOLING LOAD 9.1.x
CASE 900 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
1 | 2.441 | 3.1039 | 3.101 | 3.394 |  | 3.208 | 3.0806 | 3.4 | 3.083
2 | 2.606 | 3.1986 | 3.237 | 3.54 |  | 3.349 | 3.2028 | 3.547 | 3.221
3 | 2.623 | 3.2044 | 3.279 | 3.557 |  | 3.382 | 3.2778 | 3.573 | 3.262
4 | 2.667 | 3.3056 | 3.377 | 3.613 |  | 3.447 | 3.3306 | 3.629 | 3.366
5 | 2.744 | 3.3669 | 3.446 | 3.666 |  | 3.506 | 3.4167 | 3.687 | 3.436
6 | 2.8 | 3.3993 | 3.498 | 3.715 |  | 3.558 | 3.4694 | 3.747 | 3.484
7 | 2.834 | 3.4532 | 3.557 | 3.76 |  | 3.605 | 3.5167 | 3.797 | 3.543
8 | 2.837 | 3.376 | 3.516 | 3.749 |  | 3.608 | 3.4639 | 3.794 | 3.537
9 | 2.641 | 2.8981 | 2.974 | 3.17 |  | 3.08 | 2.8333 | 3.168 | 3.177
10 | 2.12 | 2.3463 | 2.202 | 2.32 |  | 2.348 | 2.0561 | 2.449 | 2.522
11 | 1.502 | 1.3981 | 1.034 | 0.949 |  | 1.117 | 0.79333 | 1.293 | 1.356
12 | 0.676 | 0.37698 | 0.232 | 0.101 |  | 0.3 | 0.037278 | 0.619 | 0.586
13 | 0.074 | 0 | 0 | 0 |  | 0 | 0 | 0.136 | 0
14 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.088 | 0
17 | 0.027 | 0.12409 | 0 | 0.277 |  | 0.143 | 0.13494 | 1.198 | 0.186
18 | 0.413 | 0.76691 | 0.739 | 1.216 |  | 0.91 | 0.76444 | 1.602 | 0.935
19 | 0.804 | 1.3064 | 1.14 | 1.608 |  | 1.281 | 1.1986 | 1.805 | 1.28
20 | 1.068 | 1.613 | 1.429 | 1.816 |  | 1.543 | 1.4589 | 1.943 | 1.547
21 | 1.269 | 1.9255 | 1.7 | 2.038 |  | 1.81 | 1.7008 | 2.121 | 1.81
22 | 1.502 | 2.1361 | 1.894 | 2.174 |  | 1.995 | 1.9342 | 2.227 | 1.997
23 | 1.658 | 2.2208 | 2.028 | 2.293 |  | 2.154 | 2.0922 | 2.338 | 2.124
24 | 1.749 | 2.3111 | 2.193 | 2.423 |  | 2.311 | 2.2267 | 2.458 | 2.286
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN 9.1.x
CASE 900FF
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x
TEMP (C) | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS
-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0
-5 | 0 | 0 | 1 | 2 | 0 | 0 | 3 | 4 | 1
-4 | 0 | 1 | 3 | 3 | 4 | 4 | 6 | 5 | 4
-3 | 0 | 3 | 7 | 5 | 2 | 3 | 6 | 7 | 7
-2 | 3 | 5 | 5 | 7 | 7 | 8 | 12 | 10 | 3
-1 | 3 | 6 | 10 | 7 | 5 | 5 | 13 | 18 | 14
0 | 8 | 10 | 18 | 19 | 18 | 18 | 12 | 20 | 15
1 | 6 | 17 | 17 | 19 | 10 | 20 | 12 | 12 | 16
2 | 18 | 14 | 18 | 13 | 20 | 14 | 20 | 16 | 17
3 | 18 | 19 | 19 | 15 | 15 | 19 | 18 | 25 | 20
4 | 17 | 14 | 20 | 23 | 20 | 21 | 20 | 24 | 22
5 | 18 | 25 | 30 | 28 | 24 | 27 | 26 | 27 | 31
6 | 22 | 19 | 25 | 29 | 27 | 30 | 34 | 35 | 32
7 | 31 | 33 | 37 | 28 | 28 | 33 | 29 | 45 | 40
8 | 30 | 34 | 51 | 46 | 33 | 46 | 44 | 59 | 52
9 | 42 | 42 | 59 | 62 | 57 | 61 | 55 | 73 | 60
10 | 51 | 54 | 84 | 69 | 53 | 71 | 57 | 118 | 92
11 | 67 | 72 | 107 | 111 | 89 | 116 | 95 | 134 | 127
12 | 90 | 115 | 139 | 137 | 112 | 127 | 127 | 138 | 140
13 | 115 | 137 | 153 | 141 | 142 | 157 | 143 | 173 | 168
14 | 156 | 159 | 158 | 154 | 151 | 160 | 162 | 183 | 180
15 | 172 | 165 | 206 | 188 | 178 | 207 | 183 | 234 | 241
16 | 215 | 198 | 239 | 232 | 195 | 224 | 234 | 274 | 264
17 | 244 | 245 | 274 | 253 | 248 | 255 | 273 | 298 | 267
18 | 293 | 277 | 350 | 301 | 266 | 315 | 296 | 342 | 330
19 | 338 | 317 | 322 | 336 | 332 | 347 | 356 | 352 | 373
20 | 387 | 365 | 375 | 342 | 344 | 352 | 346 | 331 | 365
21 | 398 | 358 | 392 | 362 | 361 | 366 | 388 | 334 | 348
22 | 385 | 372 | 364 | 329 | 376 | 349 | 380 | 343 | 338
23 | 396 | 341 | 370 | 348 | 366 | 357 | 366 | 349 | 354
24 | 380 | 368 | 381 | 352 | 341 | 341 | 401 | 338 | 353
25 | 417 | 357 | 432 | 361 | 397 | 392 | 404 | 404 | 380
26 | 455 | 389 | 431 | 373 | 426 | 399 | 436 | 393 | 402
27 | 459 | 420 | 415 | 415 | 418 | 403 | 465 | 396 | 425
28 | 445 | 463 | 452 | 390 | 446 | 440 | 412 | 411 | 406
29 | 459 | 419 | 410 | 405 | 432 | 396 | 408 | 391 | 399
30 | 415 | 396 | 404 | 418 | 422 | 395 | 398 | 362 | 394
31 | 406 | 393 | 342 | 401 | 389 | 360 | 335 | 342 | 350
32 | 369 | 348 | 349 | 341 | 334 | 337 | 348 | 322 | 334
33 | 339 | 315 | 309 | 330 | 338 | 306 | 310 | 291 | 326
34 | 277 | 321 | 242 | 285 | 311 | 306 | 297 | 266 | 274
35 | 230 | 303 | 197 | 246 | 262 | 256 | 202 | 210 | 236
36 | 191 | 254 | 185 | 213 | 203 | 217 | 197 | 169 | 195
37 | 164 | 195 | 136 | 156 | 189 | 166 | 161 | 151 | 151
38 | 108 | 175 | 92 | 146 | 137 | 138 | 97 | 132 | 111
39 | 71 | 99 | 74 | 112 | 103 | 97 | 86 | 85 | 59
40 | 37 | 66 | 35 | 90 | 71 | 57 | 48 | 59 | 34
41 | 15 | 32 | 16 | 58 | 35 | 31 | 22 | 32 | 10
42 | 0 | 25 | 5 | 36 | 18 | 10 | 11 | 20 | 0
43 | 0 | 5 | 0 | 18 | 5 | 1 | 2 | 1 | 0
44 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS
CODENAME: | kW: ESP; kW: BLAST; kW: DOE2; MAX: SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | Tas |  |  |  | Within
COUNTRY: | kW: UK-DMU; kW: USA/ITALY; kW: USA; MAX: USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | 9.1.x |  |  |  | Range
CASE# | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | MIN | MAX
600 | 3.437 | 1993-01-04 | 5 | 3.94 | JAN 04 | 5 | 4.045 | JAN 04 | 5 | 4.258 | JAN 04 | 2 |  |  |  | 4.037 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.354 | JAN 04 | 2 | 4.015 | 4 Jan | 5 | 3.437 | 4.354 | YES
610 | 3.437 | 1993-01-04 | 5 | 3.941 | JAN 04 | 5 | 4.034 | JAN 04 | 5 | 4.258 | JAN 04 | 2 |  |  |  | 4.037 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.354 | JAN 04 | 2 | 4.015 | 4 Jan | 5 | 3.437 | 4.354 | YES
620 | 3.591 | 1993-01-04 | 6 | 3.941 | JAN 04 | 5 | 4.046 | JAN 04 | 5 | 4.277 | JAN 04 | 2 |  |  |  | 4.277 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 | 4.016 | 4 Jan | 5 | 3.591 | 4.379 | YES
630 | 3.592 | 1993-01-04 | 7 | 3.941 | JAN 04 | 5 | 4.025 | JAN 04 | 5 | 4.28 | JAN 04 | 2 |  |  |  | 4.278 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 |  |  |  | 4.016 | 4 Jan | 5 | 3.592 | 4.28 | YES
640 | 5.232 | 1993-01-04 | 7 | 5.486 | JAN 04 | 8 | 5.943 | JAN 04 | 8 | 6.53 | JAN 04 | 8 |  |  |  | 6.347 | JAN 04 | 8 | 5.7222 | Jan-04 | 8 | 6.954 | JAN 04 | 8 | 6.419 | 4 Jan | 8 | 5.232 | 6.954 | YES
650 | kW: 0; kW: 0; kW: 0; MIN: 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | YES
900 | 2.85 | 1993-01-04 | 7 | 3.453 | JAN 04 | 7 | 3.557 | JAN 04 | 7 | 3.76 | JAN 04 | 7 |  |  |  | 3.608 | JAN 04 | 8 | 3.5167 | Jan-04 | 7 | 3.797 | JAN 04 | 7 | 3.543 | 4 Jan | 7 | 2.85 | 3.797 | YES
910 | 2.858 | 1993-01-04 | 7 | 3.456 | JAN 04 | 7 | 3.564 | JAN 04 | 7 | 3.764 | JAN 04 | 7 |  |  |  | 3.618 | JAN 04 | 8 | 3.5361 | Jan-04 | 7 | 3.801 | JAN 04 | 7 | 3.546 | 4 Jan | 7 | 2.858 | 3.801 | YES
920 | 3.308 | 1993-01-04 | 7 | 3.703 | JAN 04 | 7 | 3.805 | JAN 04 | 7 | 4.013 | JAN 04 | 7 |  |  |  | 4.029 | JAN 04 | 7 | 3.7083 | Jan-04 | 7 | 4.061 | JAN 04 | 7 | 3.764 | 4 Jan | 7 | 3.308 | 4.061 | YES
930 | 3.355 | 1993-01-04 | 7 | 3.732 | JAN 04 | 7 | 3.832 | JAN 04 | 7 | 4.042 | JAN 04 | 7 |  |  |  | 4.064 | JAN 04 | 7 | 3.7444 | Jan-04 | 7 |  |  |  | 3.793 | 4 Jan | 7 | 3.355 | 4.064 | YES
940 | 3.98 | 1993-01-04 | 7 | 5.028 | JAN 04 | 8 | 5.665 | JAN 04 | 8 | 6.116 | JAN 04 | 8 |  |  |  | 6.117 | JAN 04 | 8 | 5.1222 | Jan-03 | 9 | 6.428 | JAN 04 | 8 | 6.016 | 4 Jan | 8 | 3.98 | 6.428 | YES
950 | kW: 0; kW: 0; kW: 0; MIN: 0 |  |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | YES
960 | 2.41 | 1993-01-04 | 7 | 2.751 | JAN 04 | 8 | 2.727 | JAN 04 | 8 | 2.863 | JAN 04 | 8 |  |  |  | 2.852 | JAN 04 | 8 | 2.522 | Jan-04 | 8 | 2.779 | JAN 04 | 8 | 2.776 | 4 Jan | 8 | 2.41 | 2.863 | YES
195 | kW: 2.004; kW: 1993-01-04; kW: 2 | [13 empty] | 2.164 | 4 Jan | 7 | 2.004 | 2.004
200 | kW: 2.651; kW: 1993-01-04; kW: 5 | [13 empty] | 2.601 | 4 Jan | 5 | 2.651 | 2.651
210 | kW: 2.701; kW: 1993-01-04; kW: 5; kW: 2.973; kW: JAN 04; kW: 5 | [7 empty] | 2.9806 | Jan-04 | 5 | 3.325 | JAN 04 | 2 | 3.047 | 4 Jan | 5 | 2.701 | 3.325
215 | kW: 2.787; kW: 1993-01-04; kW: 5 | [13 empty] | 2.742 | 4 Jan | 7 | 2.787 | 2.787
220 | 2.867 | 1993-01-04 | 5 | 3.28 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 |  |  |  | 3.348 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2 | 3.41 | 4 Jan | 5 | 2.867 | 3.695 | YES
230 | 4.386 | 1993-01-04 | 5 | 4.984 | JAN 04 | 2 | 4.994 | JAN 04 | 2 | 5.279 | JAN 04 | 2 |  |  |  | 5.159 | JAN 04 | 2 | 4.8917 | Jan-04 | 6 | 5.107 | JAN 04 | 2 | 4.979 | 4 Jan | 5 | 4.386 | 5.279 | YES
240 | 2.685 | 1993-01-04 | 5 | 3.1 | JAN 04 | 5 | 3.282 | JAN 04 | 5 | 3.495 | JAN 04 | 2 |  |  |  | 3.159 | JAN 04 | 8 | 3.1528 | Jan-04 | 6 | 3.333 | JAN 04 | 8 | 3.228 | 4 Jan | 5 | 2.685 | 3.495 | YES
250 | 2.866 | 1993-01-04 | 5 | 3.279 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 |  |  |  | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.525 | JAN 04 | 2 | 3.41 | 4 Jan | 5 | 2.866 | 3.695 | YES
270 | 2.863 | 1993-01-04 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.738 | JAN 04 | 2 | 3.413 | 4 Jan | 5 | 2.863 | 3.738 | YES
280 | 2.864 | 1993-01-04 | 5 | 3.278 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.759 | JAN 04 | 2 | 3.413 | 4 Jan | 5 | 2.864 | 3.759 | YES
290 | 2.863 | 1993-01-04 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | 3.738 | JAN 04 | 2 | 3.413 | 4 Jan | 5 | 2.863 | 3.738 | YES
300 | 3.014 | 1993-01-04 | 6 | 3.276 | JAN 04 | 5 |  |  |  | 3.681 | JAN 04 | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | 3.77 | JAN 04 | 2 | 3.413 | 4 Jan | 5 | 3.014 | 3.77 | YES
310 | 3.015 | 1993-01-04 | 6 | 3.277 | JAN 04 | 5 |  |  |  | 3.669 | JAN 04 | 2 | [6 empty] | 3.3278 | Jan-04 | 6 |  |  |  | 3.413 | 4 Jan | 5 | 3.015 | 3.669 | YES
320 | 2.861 | 1993-01-04 | 5 | 3.275 | JAN 04 | 5 |  |  |  | 3.651 | JAN 04 | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.735 | JAN 04 | 3 | 3.412 | 4 Jan | 5 | 2.861 | 3.735 | YES
395 | 2.062 | 1993-01-04 | 7 | 2.209 | JAN 04 | 8 | 2.328 | JAN 04 | 3 | 2.385 | JAN 04 | 3 |  |  |  | 2.263 | JAN 04 | 4 | 2.2211 | Jan-04 | 8 | 2.27 | JAN 04 | 3 | 2.293 | 4 Jan | 8 | 2.062 | 2.385 | YES
400 | 2.867 | 1993-01-04 | 5 | 3.28 | JAN 04 | 5 | 3.476 | JAN 04 | 5 | 3.695 | JAN 04 | 2 |  |  |  | 3.342 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2 | 3.41 | 4 Jan | 5 | 2.867 | 3.695 | YES
410 | 3.625 | 1993-01-04 | 5 | 4.124 | JAN 04 | 5 | 4.233 | JAN 04 | 5 | 4.487 | JAN 04 | 2 |  |  |  | 4.227 | JAN 04 | 2 | 4.1139 | Jan-04 | 6 | 4.314 | JAN 04 | 2 | 4.195 | 4 Jan | 5 | 3.625 | 4.487 | YES
420 | 3.443 | 1993-01-04 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 |  |  |  | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.126 | JAN 04 | 2 | 4.013 | 4 Jan | 5 | 3.443 | 4.287 | YES
430 | 3.442 | 1993-01-04 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 |  |  |  | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.137 | JAN 04 | 2 | 4.013 | 4 Jan | 5 | 3.442 | 4.287 | YES
440 | 3.439 | 1993-01-04 | 5 | 3.942 | JAN 04 | 5 |  |  |  | 4.277 | JAN 04 | 2 | [6 empty] | 3.9306 | Jan-04 | 6 | 4.376 | JAN 04 | 2 | 4.015 | 4 Jan | 5 | 3.439 | 4.376 | YES
800 | 3.227 | 1993-01-04 | 5 | 3.793 | JAN 04 | 7 | 3.909 | JAN 04 | 7 | 4.138 | JAN 04 | 2 |  |  |  | 3.902 | JAN 04 | 8 | 3.7861 | Jan-04 | 7 | 3.939 | JAN 04 | 7 | 3.846 | 4 Jan | 7 | 3.227 | 4.138 | YES
810 | 2.979 | 1993-01-04 | 7 | 3.566 | JAN 04 | 7 |  |  |  | 3.915 | JAN 04 | 7 | [6 empty] | 3.6056 | Jan-04 | 7 | 3.963 | JAN 04 | 7 | 3.646 | 4 Jan | 7 | 2.979 | 3.963 | YES
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS
CODENAME: | kW: ESP; kW: BLAST; kW: DOE2; MAX: SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | Tas |  |  |  | Within
COUNTRY: | kW: UK-DMU; kW: USA/ITALY; kW: USA; MAX: USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | 9.1.x |  |  |  | Range
CASE# | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | KW | DATE | HR | KW | DATE | HR | MIN | MAX
600 | 6.194 | 1993-10-17 | 13 | 5.965 | OCT 16 | 14 | 6.656 | OCT 16 | 13 | 6.827 | OCT 16 | 14 |  |  |  | 6.286 | NOV 25 | -6.194 | 6.4861 | Oct-16 | 14 | 6.812 | OCT 17 | 14 | 6.115 | 17 Oct | 14 | 5.965 | 6.827 | YES
610 | 5.669 | 1993-11-25 | 13 | 5.824 | NOV 25 | 14 | 6.064 | JAN 13 | 14 | 6.371 | NOV 25 | 14 |  |  |  | 6.17 | NOV 25 | -5.669 | 5.675 | 1925-11-01 | 14 | 6.146 | OCT 17 | 14 | 5.829 | 25 Nov | 14 | 5.669 | 6.371 | YES
620 | 3.634 | 1993-07-26 | 16 | 4.075 | JUL 26 | 17 | 4.43 | JUL 26 | 17 | 4.593 | JUL 26 | 17 |  |  |  | 4.297 | JUL 26 | -3.634 | 4.275 | 1926-07-01 | 17 | 5.096 | JUL 26 | 16 | 3.889 | 26 Jul | 17 | 3.634 | 5.096 | YES
630 | 3.072 | 1993-07-26 | 16 | 3.704 | JUL 26 | 17 | 3.588 | JUL 26 | 17 | 4.116 | JUL 26 | 17 |  |  |  | 3.665 | JUL 26 | -3.072 | 3.6083 | 1926-07-01 | 17 |  |  |  | 3.442 | 26 Jul | 17 | 3.072 | 4.116 | YES
640 | 6.161 | 1993-10-17 | 13 | 5.892 | OCT 16 | 14 | 6.576 | OCT 16 | 14 | 6.776 | OCT 16 | 14 |  |  |  | 6.25 | NOV 25 | -6.161 | 6.4417 | Oct-16 | 14 | 6.771 | OCT 17 | 14 | 6.073 | 17 Oct | 14 | 5.892 | 6.776 | YES
650 | 6.031 | 1993-10-17 | 13 | 5.831 | OCT 16 | 14 | 6.516 | OCT 16 | 14 | 6.671 | OCT 16 | 14 |  |  |  | 6.143 | NOV 25 | -6.031 | 6.3778 | Oct-17 | 14 | 6.679 | OCT 17 | 14 | 5.958 | 17 Oct | 14 | 5.831 | 6.679 | YES
900 | 2.888 | 1993-10-17 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | OCT 17 | 14 |  |  |  | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 | 3.114 | 17 Oct | 15 | 2.888 | 3.871 | YES
910 | 1.896 | 1993-10-17 | 15 | 2.5 | OCT 21 | 15 | 2.336 | OCT 17 | 15 | 3.277 | OCT 17 | 15 |  |  |  | 2.786 | OCT 17 | -1.896 | 2.7917 | Oct-17 | 15 | 3.147 | OCT 17 | 15 | 2.404 | 17 Oct | 15 | 1.896 | 3.277 | YES
920 | 2.385 | 1993-07-26 | 16 | 2.933 | JUL 26 | 17 | 3.109 | JUL 26 | 17 | 3.487 | JUL 26 | 17 |  |  |  | 3.071 | JUL 26 | -2.385 | 3.05 | 1926-07-01 | 17 | 3.505 | JUL 26 | 17 | 2.769 | 26 Jul | 17 | 2.385 | 3.505 | YES
930 | 1.873 | 1993-07-26 | 17 | 2.546 | JUL 26 | 17 | 2.388 | JUL 26 | 18 | 3.08 | JUL 26 | 17 |  |  |  | 2.486 | JUL 26 | -1.873 | 2.4983 | 1926-07-01 | 17 |  |  |  | 2.404 | 26 Jul | 18 | 1.873 | 3.08 | YES
940 | 2.888 | 1993-10-17 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | OCT 17 | 14 |  |  |  | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 | 3.114 | 17 Oct | 15 | 2.888 | 3.871 | YES
950 | 2.033 | 1993-09-02 | 14 | 2.621 | SEP 02 | 15 | 2.664 | SEP 2 | 15 | 3.17 | SEP 02 | 14 |  |  |  | 2.677 | SEP 02 | -2.033 | 2.6861 | Sep-02 | 15 | 2.867 | SEP 02 | 14 | 2.527 | 2 Sep | 15 | 2.033 | 3.17 | YES
960 | 0.953 | 1993-08-16 | 16 | 1.144 | JUL 26 | 16 | 1.057 | JUL 26 | 16 | 1.37 | JUL 26 | 16 |  |  |  | 1.179 | JUL 26 | 16 | 1.378 | 1926-07-01 | 16 | 1.403 | JUL 26 | 16 | 1.116 | 27 Jul | 16 | 0.953 | 1.403 | YES
195 | kW: 0.651; kW: 1993-07-26; kW: 15 | [13 empty] | 0.777 | 26 Jul | 16 | 0.651 | 0.651
200 | kW: 0.863; kW: 1993-08-16; kW: 14 | [13 empty] | 0.93 | 26 Jul | 16 | 0.863 | 0.863
210 | kW: 0.476; kW: 1993-08-16; kW: 16; kW: 1.017; kW: JUL 26; kW: 15 | [7 empty] | 1.0678 | 1926-07-01 | 16 | 1.142 | JUL 26 | 15 | 0.944 | 27 Jul | 15 | 0.476 | 1.142
215 | kW: 1.007; kW: 1993-08-11; kW: 14 | [13 empty] | 0.978 | 26 Jul | 16 | 1.007 | 1.007
220 | 0.56 | 1993-07-27 | 15 | 1.166 | JUL 26 | 15 | 0.937 | JUL 27 | 14 | 1.34 | JUL 26 | 15 |  |  |  | 1.215 | JUL 26 | -0.56 | 1.1789 | 1926-07-01 | 16 | 1.213 | JUL 26 | 15 | 1.059 | 27 Jul | 15 | 0.56 | 1.34 | YES
230 | 1.059 | 1993-07-27 | 15 | 1.646 | JUL 26 | 15 | 1.455 | JUL 27 | 14 | 1.875 | JUL 26 | 15 |  |  |  | 1.7 | JUL 26 | -1.059 | 1.7078 | 1926-07-01 | 16 | 1.749 | JUL 26 | 15 | 1.581 | 27 Jul | 15 | 1.059 | 1.875 | YES
240 | 0.739 | 1993-07-27 | 15 | 1.347 | JUL 26 | 15 | 1.119 | JUL 27 | 14 | 1.54 | JUL 26 | 15 |  |  |  | 1.398 | JUL 26 | -0.739 | 1.3614 | 1926-07-01 | 16 | 1.397 | JUL 26 | 15 | 1.241 | 27 Jul | 15 | 0.739 | 1.54 | YES
250 | 3.36 | 1993-09-05 | 12 | 3.036 | SEP 05 | 12 | 2.605 | SEP 5 | 11 | 2.59 | AUG 26 | 14 |  |  |  | 2.258 | AUG 26 | -3.36 | 3.2278 | Sep-05 | 13 | 4.912 | SEP 05 | 12 | 2.73 | 5 Sep | 12 | 2.258 | 4.912 | YES
270 | 6.356 | 1993-11-25 | 13 | 6.641 | NOV 25 | 14 |  |  |  | 7.234 | OCT 16 | 14 | [6 empty] | 6.7639 | Oct-17 | 14 | 6.867 | OCT 16 | 14 | 6.528 | 25 Nov | 14 | 6.356 | 7.234 | YES
280 | 4.444 | 1993-10-17 | 13 | 4.631 | NOV 25 | 13 |  |  |  | 5.22 | OCT 16 | 14 | [6 empty] | 4.7861 | Oct-16 | 14 | 5.236 | OCT 16 | 14 | 4.514 | 25 Nov | 14 | 4.444 | 5.236 | YES
290 | 6.269 | 1993-01-13 | 13 | 6.555 | NOV 25 | 14 |  |  |  | 6.976 | NOV 25 | 14 | [6 empty] | 6.2028 | 1925-11-01 | 14 | 6.621 | NOV 25 | 14 | 6.43 | 25 Nov | 14 | 6.2028 | 6.976 | YES
300 | 3.404 | 1993-07-26 | 16 | 4.093 | JUL 26 | 17 |  |  |  | 4.657 | JUL 26 | 17 | [6 empty] | 4.2778 | 1926-07-01 | 17 | 4.929 | JUL 26 | 17 | 3.874 | 26 Jul | 17 | 3.404 | 4.929 | YES
310 | 2.848 | 1993-07-26 | 16 | 3.749 | JUN 30 | 17 |  |  |  | 4.164 | JUL 26 | 17 | [6 empty] | 3.5889 | 1926-07-01 | 17 |  |  |  | 3.467 | 26 Jul | 18 | 2.848 | 4.164 | YES
320 | 5.701 | 1993-11-25 | 13 | 5.946 | NOV 25 | 14 |  |  |  | 6.553 | OCT 16 | 14 | [6 empty] | 6.1778 | Oct-17 | 14 | 6.141 | OCT 16 | 14 | 5.893 | 25 Nov | 14 | 5.701 | 6.553 | YES
395 | 0 |  |  | 0.362 | JUL 26 | 18 | 0 |  |  | 0.394 | JUL 26 | 17 |  |  |  | 0.356 | JUL 26 | 18 | 0.3625 | 1926-07-01 | 18 | 0.345 | JUL 26 | 18 | 0.19 | 27 Jul | 17 | 0 | 0.394 | YES
400 | 0 |  |  | 0.581 | JUL 26 | 17 | 0.265 | JUL 27 | 17 | 0.666 | JUL 26 | 16 |  |  |  | 0.612 | JUL 26 | 17 | 0.61333 | 1926-07-01 | 17 | 0.572 | JUL 26 | 17 | 0.422 | 27 Jul | 17 | 0 | 0.666 | YES
410 | 0.035 | 1993-07-27 | 16 | 0.699 | JUL 26 | 17 | 0.413 | JUL 27 | 17 | 0.814 | JUL 26 | 15 |  |  |  | 0.724 | JUL 26 | -0.035 | 0.74306 | 1926-07-01 | 17 | 0.71 | JUL 26 | 17 | 0.563 | 27 Jul | 16 | 0.035 | 0.814 | YES
420 | 0.258 | 1993-07-27 | 15 | 0.923 | JUL 26 | 15 | 0.631 | JUL 27 | 15 | 1.047 | JUL 26 | 15 |  |  |  | 0.938 | JUL 26 | -0.258 | 0.93778 | 1926-07-01 | 16 | 0.921 | JUL 26 | 15 | 0.783 | 27 Jul | 15 | 0.258 | 1.047 | YES
430 | 1.493 | 1993-08-16 | 14 | 1.772 | AUG 26 | 14 | 1.427 | AUG 16 | 14 | 1.762 | JUL 26 | 15 |  |  |  | 1.575 | JUL 26 | -1.493 | 1.7983 | 1905-09-01 | 13 | 2.578 | SEP 05 | 12 | 1.485 | 16 Aug | 14 | 1.427 | 2.578 | YES
440 | 4.546 | 1993-10-17 | 13 | 4.424 | OCT 16 | 14 |  |  |  | 5.053 | OCT 16 | 14 | [6 empty] | 4.6861 | Oct-16 | 14 | 5.278 | OCT 17 | 14 | 4.449 | 17 Oct | 14 | 4.424 | 5.278 | YES
800 | 0.585 | 1993-07-27 | 14 | 0.967 | AUG 16 | 14 | 0.743 | JUL 28 | 14 | 1.352 | JUL 27 | 14 |  |  |  | 1.028 | JUL 27 | -0.585 | 0.98278 | Aug-16 | 14 | 1.358 | SEP 05 | 12 | 0.845 | 28 Jul | 14 | 0.585 | 1.358 | YES
810 | 1.852 | 1993-09-02 | 14 | 2.357 | AUG 26 | 14 |  |  |  | 2.991 | SEP 02 | 14 | [6 empty] | 2.3436 | Sep-02 | 14 | 2.862 | SEP 02 | 14 | 2.289 | 2 Sep | 14 | 1.852 | 2.991 | YES
FREE-FLOAT TEMPERATURE OUTPUT
MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | kW: ESP; kW: BLAST; kW: DOE2; MAX: SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | Tas |  |  |  | Within
COUNTRY: | kW: UK-DMU; kW: USA/ITALY; kW: USA; MAX: USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | 9.1.x |  |  |  | Range
CASE# | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | MIN | MAX
600FF | 64.929 | 1993-10-17 | 15 | 65.11 | OCT 16 | 15 | 69.5 | OCT 17 | 15 | 68.6 | OCT 16 | 15 |  |  |  | 64.9 | OCT 16 | 16 | 65.25 | Oct-17 | 16 | 65.25 | OCT 15 | 16 | 64.029 | 17 Oct | 16 | 64.9 | 69.5 | NO
900FF | 41.812 | 1993-10-17 | 15 | 43.44 | SEP 02 | 16 | 42.7 | SEP 02 | 15 | 44.8 | SEP 02 | 15 |  |  |  | 43 | SEP 02 | 15 | 42.46 | Oct-17 | 15 | 43.17 | SEP 15 | 15 | 41.92 | 2 Sep | 15 | 41.812 | 44.8 | YES
650FF | 63.236 | 1993-10-17 | 15 | 63.45 | OCT 16 | 15 | 68.2 | OCT 17 | 15 | 67 | OCT 16 | 15 |  |  |  | 63.3 | OCT 16 | 16 | 63.74 | Oct-17 | 16 | 63.82 | OCT 16 | 16 | 62.526 | 17 Oct | 16 | 63.236 | 68.2 | NO
950FF | 35.54 | 1993-09-02 | 16 | 36.23 | SEP 02 | 16 | 35.9 | SEP 02 | 16 | 38.5 | SEP 02 | 15 |  |  |  | 36.1 | SEP 02 | 16 | 35.67 | Sep-02 | 15 | 37.58 | SEP 15 | 16 | 35.636 | 2 Sep | 16 | 35.54 | 38.5 | YES
960 | 48.943 | 1993-10-17 | 15 | 48.88 | OCT 06 | 15 | 49 | OCT 17 | 15 | 51 | OCT 17 | 15 |  |  |  | 50.2 | OCT 17 | 15 | 55.34 | Oct-17 | 15 | 48.92 | OCT 15 | 15 | 48.559 | 17 Oct | 15 | 48.88 | 55.34 | NO
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | kW: ESP; kW: BLAST; kW: DOE2; MAX: SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | Tas |  |  |  | Within
COUNTRY: | kW: UK-DMU; kW: USA/ITALY; kW: USA; MAX: USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | 9.1.x |  |  |  | Range
CASE# | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | MIN | MAX
600FF | -15.565 | 1993-01-04 | 7 | -17.05 | JAN 04 | 8 | -18.8 | JAN 04 | 8 | -18 | JAN 04 | 7 |  |  |  | -17.8 | JAN 04 | 8 | -17.81 | Jan-04 | 7 | -18.47 | JAN 08 | 9 | -18.854 | 4 Jan | 8 | -18.8 | -15.565 | NO
900FF | -1.647 | 1993-01-04 | 8 | -3.15 | JAN 04 | 8 | -4.3 | JAN 04 | 8 | -4.5 | JAN 04 | 8 |  |  |  | -4 | JAN 04 | 8 | -6.38 | Jan-04 | 8 | -5.64 | JAN 08 | 9 | -4.354 | 4 Jan | 8 | -6.38 | -1.647 | YES
650FF | -22.564 | 1993-01-04 | 6 | -22.96 | JAN 04 | 7 | -21.6 | JAN 04 | 2 | -23 | JAN 04 | 2 |  |  |  | -22.9 | JAN 04 | 2 | -22.83 | Jan-04 | 7 | -22.91 | JAN 02 | 23 | -23.025 | 4 Jan | 7 | -23 | -21.6 | NO
950FF | -19.484 | 1993-01-04 | 6 | -20.04 | JAN 04 | 7 | -18.6 | JAN 04 | 7 | -19.7 | JAN 04 | 7 |  |  |  | -20.2 | JAN 04 | 7 | -19.34 | Jan-04 | 7 | -19.96 | JAN 07 | 22 | -19.954 | 4 Jan | 7 | -20.2 | -18.6 | YES
960 | 2.729 | 1993-02-06 | 6 | 1.63 | FEB 06 | 7 | 3.9 | FEB 06 | 7 | 3.1 | FEB 06 | 7 |  |  |  | 1.4 | FEB 06 | 6 | -2.82 | Jan-04 | 8 | -0.39 | FEB 05 | 7 | 0.938 | 4 Jan | 8 | -2.82 | 3.9 | YES
AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | kW: ESP; kW: BLAST; kW: DOE2; MAX: SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | Tas |  |  |  | Within
COUNTRY: | kW: UK-DMU; kW: USA/ITALY; kW: USA; MAX: USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | 9.1.x |  |  |  | Range
CASE# | kW: TMP (C); kW: TMP (C); kW: TMP (C); MIN: TMP (C) |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | MIN | MAX
600FF | kW: 25.126; kW: 25.43; kW: 24.6; MIN: 25.48 |  | 25.93 |  |  | 25.2 |  |  | 24.49 |  |  | 24.22 |  |  | 24.585 |  |  | 24.22 | 25.93 | YES
900FF | kW: 25.453; kW: 25.93; kW: 24.7; MIN: 25.49 |  | 25.72 |  |  | 25.2 |  |  | 24.47 |  |  | 24.45 |  |  | 24.638 |  |  | 24.45 | 25.93 | YES
650FF | kW: 18.234; kW: 18.69; kW: 19.1; MIN: 18.96 |  | 19.62 |  |  | 18.4 |  |  | 17.99 |  |  | 18.36 |  |  | 18.101 |  |  | 17.99 | 19.62 | YES
950FF | kW: 14.14; kW: 14.26; kW: 14.3; MIN: 14.97 |  | 14.29 |  |  | 14 |  |  | 14.53 |  |  | 14.64 |  |  | 13.938 |  |  | 14 | 14.97 | NO
960 | kW: 27.49; kW: 27.72; kW: 28; MIN: 28.69 |  | 28.54 |  |  | 28 |  |  | 28.96 |  |  | 26.43 |  |  | 27.282 |  |  | 26.43 | 28.96 | YES
LOW MASS BASIC SENSITIVITY TESTS
ANNUAL HEATING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
610-600 | 0.059 | 0.033 | 0.077 | 0.054 | 0.024 | 0.089 | 0.098 | 0.021 | 0.039 | 0.021 | 0.098 | YES
620-600 | 0.317 | 0.276 | 0.235 | 0.328 | 0.138 | 0.682 | 0.201 | 0.366 | 0.331 | 0.138 | 0.682 | YES
630-620 | 0.437 | 0.31 | 0.525 | 0.329 | 0.267 | 0.531 | 0.551 |  | 0.323 | 0.267 | 0.551 | YES
640-600 | -1.545 | -1.885 | -2.166 | -1.971 | -1.793 | -1.817 | -1.829 | -2.053 | -1.863 | -2.166 | -1.545 | YES
ANNUAL COOLING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
610-600 | -2.222 | -1.582 | -2.227 | -1.83 | -2.186 | -1.728 | -1.891 | -1.272 | -1.727 | -2.227 | -1.272 | YES
620-600 | -2.72 | -2.341 | -2.745 | -2.645 | -2.96 | -2.481 | -2.591 | -2.427 | -2.657 | -2.96 | -2.341 | YES
630-620 | -1.288 | -0.984 | -1.845 | -1.14 | -1.303 | -1.522 | -1.485 |  | -0.958 | -1.845 | -0.984 | NO
640-600 | -0.185 | -0.25 | -0.32 | -0.252 | -0.153 | -0.245 | -0.246 | -0.27 | -0.244 | -0.32 | -0.153 | YES
650-600 | -1.321 | -1.293 | -1.284 | -1.384 | -1.419 | -1.404 | -1.373 | -1.322 | -1.376 | -1.419 | -1.284 | YES
PEAK HEATING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
610-600 | 0 | 0.001 | -0.011 | 0 |  | 0 | -0.0083333 | 0 | 0 | -0.011 | 0.001 | YES
620-600 | 0.154 | 0.001 | 0.001 | 0.019 |  | 0.24 | -0.0083333 | 0.025 | 0.001 | -0.0083333 | 0.24 | YES
630-620 | 0.001 | 0 | -0.021 | 0.003 |  | 0.001 | 0 |  | 0 | -0.021 | 0.003 | YES
640-600 | 1.795 | 1.546 | 1.898 | 2.272 |  | 2.31 | 1.7917 | 2.6 | 2.404 | 1.546 | 2.6 | YES
PEAK COOLING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
610-600 | -0.525 | -0.141 | -0.592 | -0.456 |  | -0.116 | -0.81111 | -0.666 | -0.286 | -0.81111 | -0.116 | YES
620-600 | -2.56 | -1.89 | -2.226 | -2.234 |  | -1.989 | -2.2111 | -1.716 | -2.226 | -2.56 | -1.716 | YES
630-620 | -0.562 | -0.371 | -0.842 | -0.477 |  | -0.632 | -0.66667 |  | -0.447 | -0.842 | -0.371 | YES
640-600 | -0.033 | -0.073 | -0.08 | -0.051 |  | -0.036 | -0.044444 | -0.041 | -0.042 | -0.08 | -0.033 | YES
650-600 | -0.163 | -0.134 | -0.14 | -0.156 |  | -0.143 | -0.10833 | -0.133 | -0.157 | -0.163 | -0.10833 | YES
HIGH MASS BASIC SENSITIVITY TESTS
ANNUAL HEATING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
900-600 | -3.126 | -3.163 | -3.837 | -3.329 | -3.608 | -3.152 | -3.217 | -3.321 | -3.316 | -3.837 | -3.126 | YES
910-900 | 0.405 | 0.252 | 0.382 | 0.277 | 0.294 | 0.333 | 0.442 | 0.179 | 0.285 | 0.179 | 0.442 | YES
920-900 | 2.143 | 2.142 | 2.383 | 2.196 | 2.07 | 2.505 | 2.121 | 2.259 | 2.273 | 2.07 | 2.505 | YES
930-920 | 0.83 | 0.595 | 1.08 | 0.662 | 0.67 | 0.933 | 0.964 |  | 0.639 | 0.595 | 1.08 | YES
940-900 | -0.377 | -0.589 | -0.633 | -0.666 | -0.577 | -0.551 | -0.575 | -0.718 | -0.559 | -0.718 | -0.377 | YES
960-900 | 1.141 | 1.054 | 1.056 | 0.987 | 0.863 | 1.213 | 1.718 | 0.775 | 0.819 | 0.775 | 1.718 | YES
ANNUAL COOLING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
900-600 | -4.005 | -3.833 | -4.624 | -4.113 | -4.549 | -3.92 | -4.007 | -4.179 | -4.036 | -4.624 | -3.833 | YES
910-900 | -1.311 | -1.067 | -1.479 | -1.293 | -1.561 | -1.144 | -1.159 | -0.832 | -1.13 | -1.561 | -0.832 | YES
920-900 | -0.292 | 0.016 | -0.015 | -0.222 | -0.323 | -0.115 | -0.067 | 0.014 | -0.191 | -0.323 | 0.016 | YES
930-920 | -0.801 | -0.682 | -1.174 | -0.77 | -0.854 | -1.018 | -1.002 |  | -0.604 | -1.174 | -0.682 | NO
940-900 | -0.053 | -0.064 | -0.115 | -0.129 | -0.174 | -0.083 | -0.102 | -0.083 | -0.076 | -0.174 | -0.053 | YES
950-900 | -1.745 | -2.074 | -1.917 | -2.244 | -2.826 | -2.021 | -1.9244 | -1.828 | -1.811 | -2.826 | -1.745 | YES
960-900 | -1.644 | -1.934 | -2.027 | -2.362 | -2.697 | -1.929 | -2.0737 | -1.813 | -1.763 | -2.697 | -1.644 | YES
PEAK HEATING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
900-600 | -0.587 | -0.487 | -0.488 | -0.498 |  | -0.429 | -0.41389 | -0.557 | -0.472 | -0.587 | -0.41389 | YES
910-900 | 0.008 | 0.003 | 0.007 | 0.004 |  | 0.01 | 0.019444 | 0.004 | 0.003 | 0.003 | 0.019444 | YES
920-900 | 0.458 | 0.25 | 0.248 | 0.253 |  | 0.421 | 0.19167 | 0.264 | 0.221 | 0.19167 | 0.458 | YES
930-920 | 0.047 | 0.029 | 0.027 | 0.029 |  | 0.035 | 0.036111 |  | 0.029 | 0.027 | 0.047 | YES
940-900 | 1.13 | 1.575 | 2.108 | 2.356 |  | 2.509 | 1.6056 | 2.631 | 2.473 | 1.13 | 2.631 | YES
960-900 | -0.44 | -0.702 | -0.83 | -0.897 |  | -0.756 | -0.99467 | -1.018 | -0.767 | -1.018 | -0.44 | YES
PEAK COOLING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
900-600 | -3.306 | -2.81 | -3.198 | -2.956 |  | -2.952 | -2.9194 | -3.355 | -3.001 | -3.355 | -2.81 | YES
910-900 | -0.992 | -0.655 | -1.122 | -0.594 |  | -0.548 | -0.775 | -0.31 | -0.71 | -1.122 | -0.31 | YES
920-900 | -0.503 | -0.222 | -0.349 | -0.384 |  | -0.263 | -0.51667 | 0.048 | -0.345 | -0.51667 | 0.048 | YES
930-920 | -0.512 | -0.387 | -0.721 | -0.407 |  | -0.585 | -0.55167 |  | -0.365 | -0.721 | -0.387 | NO
940-900 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | YES
950-900 | -0.855 | -0.534 | -0.794 | -0.701 |  | -0.657 | -0.88056 | -0.59 | -0.587 | -0.88056 | -0.534 | YES
960-900 | -1.935 | -2.011 | -2.401 | -2.501 |  | -2.155 | -2.1887 | -2.054 | -1.998 | -2.501 | -1.935 | YES
LOW MASS IN-DEPTH (CASES 195 THRU 320) SENSITIVITY TESTS
ANNUAL HEATING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
200-195 | kW: 1.085; KW: 0.928; MIN: 1.085; MAX: 1.085
210-200 | kW: 1.204; KW: 1.314; MIN: 1.204; MAX: 1.204
220-215 | kW: 1.397; KW: 1.826; MIN: 1.397; MAX: 1.397
215-200 | kW: 0.295; KW: 0.29; MIN: 0.295; MAX: 0.295
220-210 | 0.488 | 0.656 |  |  |  |  | 0.743 | 0.47 | 0.802 | 0.47 | 0.743
230-220 | 3.432 | 3.525 | 3.456 | 3.531 | 3.522 | 3.615 | 3.543 | 3.527 | 3.572 | 3.432 | 3.615 | YES
240-220 | -1.295 | -1.206 | -1.339 | -1.333 | -1.341 | -1.228 | -1.221 | -1.203 | -1.277 | -1.341 | -1.203 | YES
250-220 | -2.193 | -1.476 | -1.763 | -1.494 | -1.474 | -1.448 | -1.533 | -1.699 | -1.557 | -2.193 | -1.448 | YES
270-220 | -2.434 | -2.285 |  | -2.761 | -2.207 |  | -2.25 | -1.948 | -2.526 | -2.761 | -1.948 | YES
280-270 | 0.165 | 0.195 |  | 0.596 | 0.228 |  | 0.232 | 0.352 | 0.289 | 0.165 | 0.596 | YES
320-270 | -0.651 | -0.721 |  | -0.714 | -0.779 |  | -0.699 | -0.649 | -0.762 | -0.779 | -0.649 | YES
290-270 | 0.067 | 0.029 |  | 0.065 | 0.022 |  | 0.085 | 0.02 | 0.037 | 0.02 | 0.085 | YES
300-270 | 0.251 | 0.147 |  | 0.246 | 0.044 |  | 0.077 | 0.297 | 0.214 | 0.044 | 0.297 | YES
310-300 | 0.46 | 0.25 |  | 0.263 | 0.201 |  | 0.486 |  | 0.17 | 0.201 | 0.486 | NO
ANNUAL COOLING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
200-195 | kW: 0.156; KW: 0.105; MIN: 0.156; MAX: 0.156
210-200 | kW: -0.408; KW: -0.101; MIN: -0.408; MAX: -0.408
220-215 | kW: -0.453; KW: -0.069; MIN: -0.453; MAX: -0.453
215-200 | kW: 0.069; KW: 0.027; MIN: 0.069; MAX: 0.069
220-210 | 0.024 | 0.088 |  |  |  |  | 0.0689 | 0.042 | 0.059 | 0.024 | 0.088
230-220 | 0.268 | 0.275 | 0.293 | 0.304 | 0.304 | 0.286 | 0.3032 | 0.302 | 0.304 | 0.268 | 0.304 | YES
240-220 | 0.229 | 0.371 | 0.261 | 0.412 | 0.411 | 0.374 | 0.3772 | 0.362 | 0.318 | 0.229 | 0.412 | YES
250-220 | 3.027 | 1.844 | 1.778 | 2.097 | 2.096 | 1.752 | 1.9472 | 2.697 | 1.67 | 1.752 | 3.027 | NO
270-220 | 7.342 | 7.969 |  | 9.001 | 9.515 |  | 8.0272 | 8.031 | 8.017 | 7.342 | 9.515 | YES
280-270 | -2.655 | -2.775 |  | -3.317 | -3.236 |  | -3.003 | -2.457 | -2.926 | -3.317 | -2.457 | YES
320-270 | -2.467 | -2.764 |  | -3.103 | -3.046 |  | -2.808 | -3.051 | -2.819 | -3.103 | -2.467 | YES
290-270 | -2.324 | -1.659 |  | -1.957 | -2.261 |  | -2.065 | -1.283 | -1.807 | -2.324 | -1.283 | YES
300-270 | -3.226 | -2.834 |  | -3.163 | -3.25 |  | -3.043 | -2.933 | -3.206 | -3.25 | -2.834 | YES
310-300 | -1.57 | -1.266 |  | -1.42 | -1.629 |  | -1.994 |  | -0.879 | -1.994 | -1.266 | NO
PEAK HEATING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
200-195 | kW: 0.647; KW: 0.437; MIN: 0.647; MAX: 0.647
210-200 | kW: 0.05; KW: 0.446; MIN: 0.05; MAX: 0.05
220-215 | kW: 0.08; KW: 0.668; MIN: 0.08; MAX: 0.08
215-200 | kW: 0.136; KW: 0.141; MIN: 0.136; MAX: 0.136
220-210 | 0.166 | 0.307 |  |  |  |  | 0.35556 | 0.195 | 0.363 | 0.166 | 0.35556
230-220 | 1.519 | 1.704 | 1.529 | 1.584 |  | 1.811 | 1.5556 | 1.587 | 1.569 | 1.519 | 1.811 | YES
240-220 | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.189 | -0.18333 | -0.187 | -0.182 | -0.2 | -0.18 | YES
250-220 | -0.001 | -0.001 | 0 | 0 |  | -0.007 | 0 | 0.005 | 0 | -0.007 | 0.005 | YES
270-220 | -0.004 | -0.003 |  | -0.034 |  |  | 0 | 0.218 | 0.003 | -0.034 | 0.218 | YES
280-270 | 0.001 | 0.001 |  | 0.024 |  |  | 0 | 0.021 | 0 | 0 | 0.024 | YES
320-270 | -0.002 | -0.002 |  | -0.01 |  |  | 0 | -0.003 | -0.001 | -0.01 | 0 | YES
290-270 | 0 | 0 |  | 0 |  |  | -0.0083333 | 0 | 0 | -0.0083333 | 0 | YES
300-270 | 0.151 | -0.001 |  | 0.02 |  |  | -0.0083333 | 0.032 | 0 | -0.0083333 | 0.151 | YES
310-300 | 0.001 | 0.001 |  | -0.012 |  |  | 0 |  | 0 | -0.012 | 0.001 | YES
PEAK COOLING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
200-195 | kW: 0.212; KW: 0.153; MIN: 0.212; MAX: 0.212
210-200 | kW: -0.387; KW: 0.014; MIN: -0.387; MAX: -0.387
220-215 | kW: -0.447; KW: 0.081; MIN: -0.447; MAX: -0.447
215-200 | kW: 0.144; KW: 0.048; MIN: 0.144; MAX: 0.144
220-210 | 0.084 | 0.149 |  |  |  |  | 0.11111 | 0.071 | 0.115 | 0.071 | 0.149
230-220 | 0.499 | 0.48 | 0.518 | 0.535 |  | 0.485 | 0.52889 | 0.536 | 0.522 | 0.48 | 0.536 | YES
240-220 | 0.179 | 0.181 | 0.182 | 0.2 |  | 0.183 | 0.1825 | 0.184 | 0.182 | 0.179 | 0.2 | YES
250-220 | 2.8 | 1.87 | 1.668 | 1.25 |  | 1.043 | 2.0489 | 3.699 | 1.671 | 1.043 | 3.699 | YES
270-220 | 5.796 | 5.475 |  | 5.894 |  |  | 5.585 | 5.654 | 5.469 | 5.475 | 5.894 | NO
280-270 | -1.912 | -2.01 |  | -2.014 |  |  | -1.9778 | -1.631 | -2.014 | -2.014 | -1.631 | YES
320-270 | -0.655 | -0.695 |  | -0.681 |  |  | -0.58611 | -0.726 | -0.635 | -0.726 | -0.58611 | YES
290-270 | -0.087 | -0.086 |  | -0.258 |  |  | -0.56111 | -0.246 | -0.098 | -0.56111 | -0.086 | YES
300-270 | -2.952 | -2.548 |  | -2.577 |  |  | -2.4861 | -1.938 | -2.654 | -2.952 | -1.938 | YES
310-300 | -0.556 | -0.344 |  | -0.493 |  |  | -0.68889 |  | -0.407 | -0.68889 | -0.344 | YES
LOW MASS IN-DEPTH (CASES 395 THRU 440) SENSITIVITY TESTS
ANNUAL HEATING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
400-395 | 1.916 | 2.276 | 2.935 | 2.767 | 2.772 | 2.32 | 2.311 | 2.487 | 2.541 | 1.916 | 2.935 | YES
410-400 | 1.696 | 1.798 | 1.736 | 1.76 | 1.761 | 1.732 | 1.77 | 1.759 | 1.779 | 1.696 | 1.798 | YES
420-410 | -1.298 | -1.263 | -1.355 | -1.361 | -1.361 | -1.245 | -1.239 | -1.222 | -1.291 | -1.361 | -1.222 | YES
430-420 | -1.869 | -1.122 | -1.324 | -1.187 | -1.187 | -1.112 | -1.197 | -1.353 | -1.171 | -1.869 | -1.112 | YES
600-430 | -1.133 | -1.715 | -2.118 | -1.952 | -1.59 | -1.78 | -1.628 | -1.148 | -1.943 | -2.118 | -1.133 | YES
440-600 | 0.153 | 0.214 |  | 0.426 | 0.215 |  | 0.226 | 0.28 | 0.265 | 0.153 | 0.426 | YES
ANNUAL COOLING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
400-395 | 0 | 0.029 | 0.002 | 0.045 | 0.044 | 0.032 | 0.03439 | 0.033 | 0.008 | 0 | 0.045 | YES
410-400 | 0 | 0.019 | 0.008 | 0.023 | 0.026 | 0.021 | 0.02239 | 0.021 | 0.012 | 0 | 0.026 | YES
420-410 | 0.011 | 0.088 | 0.041 | 0.105 | 0.104 | 0.091 | 0.09043 | 0.078 | 0.057 | 0.011 | 0.105 | YES
430-420 | 0.531 | 0.47 | 0.371 | 0.515 | 0.496 | 0.409 | 0.4599 | 0.732 | 0.352 | 0.371 | 0.732 | NO
600-430 | 5.595 | 5.816 | 6.657 | 6.574 | 7.28 | 5.929 | 5.8746 | 5.903 | 5.932 | 5.595 | 7.28 | YES
440-600 | -2.17 | -2.261 |  | -2.604 | -2.76 |  | -2.517 | -2.094 | -2.413 | -2.76 | -2.094 | YES
PEAK HEATING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
400-395 | 0.805 | 1.071 | 1.148 | 1.31 |  | 1.079 | 1.115 | 1.25 | 1.117 | 0.805 | 1.31 | YES
410-400 | 0.758 | 0.844 | 0.757 | 0.792 |  | 0.885 | 0.77778 | 0.794 | 0.785 | 0.757 | 0.885 | YES
420-410 | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.183 | -0.18333 | -0.188 | -0.182 | -0.2 | -0.18 | YES
430-420 | -0.001 | 0 | 0 | 0 |  | 0 | 0 | 0.011 | 0 | -0.001 | 0.011 | YES
600-430 | -0.005 | -0.004 | -0.005 | -0.029 |  | -0.007 | 0 | 0.217 | 0.002 | -0.029 | 0.217 | YES
440-600 | 0.002 | 0.002 |  | 0.019 |  |  | 0 | 0.022 | 0 | 0 | 0.022 | YES
PEAK COOLING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
400-395 | 0 | 0.219 | 0.265 | 0.272 |  | 0.256 | 0.25083 | 0.227 | 0.232 | 0 | 0.272 | YES
410-400 | 0.035 | 0.118 | 0.148 | 0.148 |  | 0.112 | 0.12972 | 0.138 | 0.141 | 0.035 | 0.148 | YES
420-410 | 0.223 | 0.224 | 0.218 | 0.233 |  | 0.214 | 0.19472 | 0.211 | 0.22 | 0.19472 | 0.233 | YES
430-420 | 1.235 | 0.849 | 0.796 | 0.715 |  | 0.637 | 0.86056 | 1.657 | 0.702 | 0.637 | 1.657 | YES
600-430 | 4.701 | 4.193 | 5.229 | 5.065 |  | 4.711 | 4.6878 | 4.234 | 4.63 | 4.193 | 5.229 | YES
440-600 | -1.648 | -1.541 |  | -1.774 |  |  | -1.8 | -1.534 | -1.666 | -1.8 | -1.534 | YES
HIGH MASS BASIC AND IN-DEPTH SENSITIVITY TESTS
ANNUAL HEATING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
800-430 | -0.561 | -0.535 | -0.599 | -0.567 | -0.586 | -0.501 | -0.56 | -0.649 | -0.504 | -0.649 | -0.501 | YES
900-800 | -3.698 | -4.343 | -5.356 | -4.714 | -4.612 | -4.431 | -4.285 | -3.82 | -4.755 | -5.356 | -3.698 | YES
900-810 | -0.669 | -0.836 |  | -1.107 | -0.84 |  | -0.912 | -0.921 | -0.998 | -1.107 | -0.669 | YES
910-610 | -2.78 | -2.944 | -3.532 | -3.106 | -3.338 | -2.908 | -2.873 | -3.163 | -3.07 | -3.532 | -2.78 | YES
920-620 | -1.3 | -1.297 | -1.689 | -1.461 | -1.676 | -1.329 | -1.297 | -1.428 | -1.374 | -1.689 | -1.297 | YES
930-630 | -0.907 | -1.012 | -1.134 | -1.128 | -1.273 | -0.927 | -0.884 |  | -1.058 | -1.273 | -0.884 | YES
940-640 | -1.958 | -1.867 | -2.304 | -2.024 | -2.392 | -1.886 | -1.963 | -1.986 | -2.012 | -2.392 | -1.867 | YES
ANNUAL COOLING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
800-430 | -0.429 | -0.393 | -0.367 | -0.432 | -0.462 | -0.368 | -0.4101 | -0.55 | -0.335 | -0.55 | -0.367 | NO
900-800 | 2.019 | 2.376 | 2.4 | 2.893 | 3.193 | 2.377 | 2.2777 | 2.274 | 2.231 | 2.019 | 3.193 | YES
900-810 | 1.08 | 1.195 |  | 1.454 | 1.707 |  | 1.294 | 0.975 | 1.177 | 0.975 | 1.707 | YES
910-610 | -3.094 | -3.318 | -3.876 | -3.576 | -3.924 | -3.336 | -3.275 | -3.739 | -3.439 | -3.924 | -3.094 | YES
920-620 | -1.577 | -1.476 | -1.894 | -1.69 | -1.912 | -1.554 | -1.483 | -1.738 | -1.57 | -1.912 | -1.476 | YES
930-630 | -1.09 | -1.174 | -1.223 | -1.32 | -1.463 | -1.05 | -1 |  | -1.216 | -1.463 | -1 | YES
940-640 | -3.873 | -3.647 | -4.419 | -3.99 | -4.57 | -3.758 | -3.863 | -3.992 | -3.868 | -4.57 | -3.647 | YES
950-650 | -4.429 | -4.614 | -5.257 | -4.973 | -5.956 | -4.537 | -4.5584 | -4.685 | -4.471 | -5.956 | -4.429 | YES
PEAK HEATING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
800-430 | -0.215 | -0.151 | -0.141 | -0.149 |  | -0.142 | -0.14444 | -0.198 | -0.167 | -0.215 | -0.141 | YES
900-800 | -0.377 | -0.34 | -0.352 | -0.378 |  | -0.294 | -0.26944 | -0.142 | -0.303 | -0.378 | -0.142 | YES
900-810 | -0.129 | -0.113 |  | -0.155 |  |  | -0.088889 | -0.166 | -0.103 | -0.166 | -0.088889 | YES
910-610 | -0.579 | -0.485 | -0.47 | -0.494 |  | -0.419 | -0.38611 | -0.553 | -0.469 | -0.579 | -0.38611 | YES
920-620 | -0.283 | -0.238 | -0.241 | -0.264 |  | -0.248 | -0.21389 | -0.318 | -0.252 | -0.318 | -0.21389 | YES
930-630 | -0.237 | -0.209 | -0.193 | -0.238 |  | -0.214 | -0.17778 |  | -0.223 | -0.238 | -0.17778 | YES
940-640 | -1.252 | -0.458 | -0.278 | -0.414 |  | -0.23 | -0.6 | -0.526 | -0.403 | -1.252 | -0.23 | YES
PEAK COOLING [KW]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | Tas | SUMMARY
CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | 9.1.x | MIN | MAX
800-430 | -0.908 | -0.805 | -0.684 | -0.41 |  | -0.547 | -0.81556 | -1.22 | -0.64 | -1.22 | -0.41 | YES
900-800 | 2.303 | 2.188 | 2.715 | 2.519 |  | 2.306 | 2.5839 | 2.099 | 2.269 | 2.099 | 2.715 | YES
900-810 | 1.036 | 0.798 |  | 0.88 |  |  | 1.2231 | 0.595 | 0.825 | 0.595 | 1.2231 | YES
910-610 | -3.773 | -3.324 | -3.728 | -3.094 |  | -3.384 | -2.8833 | -2.999 | -3.425 | -3.773 | -2.8833 | YES
920-620 | -1.249 | -1.142 | -1.321 | -1.106 |  | -1.226 | -1.225 | -1.591 | -1.12 | -1.591 | -1.106 | YES
930-630 | -1.199 | -1.158 | -1.2 | -1.036 |  | -1.179 | -1.11 |  | -1.038 | -1.2 | -1.036 | YES
940-640 | -3.273 | -2.737 | -3.118 | -2.905 |  | -2.916 | -2.875 | -3.314 | -2.959 | -3.314 | -2.737 | YES
950-650 | -3.998 | -3.21 | -3.852 | -3.501 |  | -3.466 | -3.6917 | -3.812 | -3.431 | -3.998 | -3.21 | YES
ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS
(ANNUAL UNSHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED INCIDENT SOLRAD)
CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | BEL/UK | FINLAND | 9.1.x
CASE#
920WEST | 0.67403 |  | 0.68119 | 0.68694 | 0.65728 | 0.64072 | 0.65382 | 0.64771 | 0.69233
900SOUTH | 0.64973 |  | 0.67114 | 0.65176 | 0.6502 | 0.62822 | 0.64663 | 0.62262 | 0.69063
ANNUAL SHADING COEFFICIENT OF WINDOW SHADING DEVICES: OVERHANGS & FINS
(1-(ANNUAL SHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED TRANSMITTED SOLRAD))
CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TRNSYS | TASE | Tas
COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | BEL/UK | FINLAND | 9.1.x
CASE#
930/920 W | 0.18169 |  | 0.34558 | 0.19594 | 0.21611 | 0.32866 | 0.33879 |  | 0.19973
910/900 S | 0.17019 |  | 0.20932 | 0.16528 | 0.18803 | 0.18251 | 0.20542 | 0.11488 | 0.1704