## A
RESULTS5-4.XLS |  |  |  | INSTRUCTIONS
Output spreadsheet for HVAC BESTEST |  |  |  | Import data so that Cell A1 of Sec5-4out.XLS is in A1 of Sheet "YD" (your data)
Check that the first value (TOTAL FURNACE LOAD GJ for HE100) lands in YD!B20.
Data should land in "YD" cells as tabulated below. Your data will then appear in columns E, I and M of Sheet A
and in rightmost column of each table on sheet Q. Chart update of "your data" is not automated.
See RESULTS5-4.DOC for spreadsheet navigation.
Cases | FURNACE LOAD | FURNACE INPUT | FUEL CONSUMPTION | FAN ENERGY | MEAN TEMP. | MAX TEMP. | MIN TEMP.
CASE HE100 | 77.76 | 77.756 | 0.00026314 | - | - | - | -
CASE HE110 | 77.76 | 97.4372 | 0.00032975 | - | - | - | -
CASE HE120 | 31.3586 | 38.6062 | 0.00013065 | - | - | - | -
CASE HE130 | 0.188 | 0.98814 | 3.3441e-06 | - | - | - | -
CASE HE140 | 31.3582 | 39.2234 | 0.00013274 | - | - | - | -
CASE HE150 | 29.8839 | 37.3059 | 0.00012625 | 431.9998 | - | - | -
CASE HE160 | 30.731 | 38.4278 | 0.00013005 | 174.724 | - | - | -
CASE HE170 | 29.8839 | 37.3059 | 0.00012625 | 473.626 | - | - | -
CASE HE210 | 42.3233 | 52.7689 | 0.00017858 | 294.2564 | 20.0456 | 20.0816 | 20.008
CASE HE220 | 40.0693 | 49.8753 | 0.00016879 | 281.8893 | 18.59 | 20.0832 | 15.0182
CASE HE230 | 34.706 | 43.4582 | 0.00014707 | 482.9875 | 15.4392 | 20.0925 | 1.0338
| TOTAL FURNACE LOAD |  |  |  | TOTAL FURNACE INPUT |  |  |  | FUEL CONSUMPTION
| GJ |  |  |  | GJ |  |  |  | m3/s
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Tas v9.4.3 | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Tas v9.4.3 | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Tas v9.4.3
| NRCAN | NRCAN | NRCAN |  | NRCAN | NRCAN | NRCAN |  | NRCAN | NRCAN | NRCAN
CASE HE100 | 77.94 | 77.75 | 77.73 | 77.76 | 77.74 | 77.7133 | 78.3043 | 77.756 | 0.000263 | 0.000263 | 0.000265 | 0.00026314
CASE HE110 | 77.94 | 77.75 | 77.73 | 77.76 | 96.9201 | 97.2156 | 97.8065 | 97.4372 | 0.000328 | 0.000329 | 0.000331 | 0.00032975
CASE HE120 | 31.25 | 31.1 | 31.12 | 31.3586 | 38.4134 | 38.2657 | 38.4134 | 38.6062 | 0.00013 | 0.0001295 | 0.00013 | 0.00013065
CASE HE130 | 0 | 0 | 0.15804 | 0.188 | 0 | 0 | 0.14479 | 0.98814 | 0 | 0 | 4.9e-07 | 3.3441e-06
CASE HE140 | 31.26 | 31.1 | 31.07 | 31.3582 | 39.0044 | 39.0044 | 38.7089 | 39.2234 | 0.000132 | 0.000132 | 0.000131 | 0.00013274
CASE HE150 | 29.88 | 29.59 | 29.55 | 29.8839 | 37.2315 | 36.936 | 36.6405 | 37.3059 | 0.000126 | 0.000125 | 0.000124 | 0.00012625
CASE HE160 | 31.26 | 30.46 | 30.48 | 30.731 | 38.118 | 38.118 | 37.8225 | 38.4278 | 0.000129 | 0.000129 | 0.000128 | 0.00013005
CASE HE170 | 29.88 | 29.59 | 29.55 | 29.8839 | 37.2315 | 36.936 | 36.6405 | 37.3059 | 0.000126 | 0.000125 | 0.000124 | 0.00012625
CASE HE210 | 41.36 | 42.04 | 42.08 | 42.3233 | 50.5284 | 52.0059 | 52.3014 | 52.7689 | 0.000171 | 0.000176 | 0.000177 | 0.00017858
CASE HE220 | 39.41 | 39.87 | 39.87 | 40.0693 | 47.8691 | 49.3465 | 49.3465 | 49.8753 | 0.000162 | 0.000167 | 0.000167 | 0.00016879
CASE HE230 | 34.32 | 34.59 | 34.49 | 34.706 | 41.3683 | 42.5503 | 43.1412 | 43.4582 | 0.00014 | 0.000144 | 0.000146 | 0.00014707
FAN ENERGY (BOTH FANS)
kWh
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Tas v9.4.3
| NRCAN | NRCAN | NRCAN
CASE HE150 | 432 | 433.3 | 432.1 | 431.9998
CASE HE160 | 170.2 | 172.2 | 172.3 | 174.724
CASE HE170 | 473.4 | 473.1 | 473.3 | 473.626
CASE HE210 | 281.6 | 291.4 | 299.2 | 294.2564
CASE HE220 | 268.3 | 276.1 | 282.2 | 281.8893
CASE HE230 | 458.3 | 431.4 | 480 | 482.9875
| MEAN ZONE TEMPERATURE |  |  |  | MAXIMUM ZONE TEMPERATURE |  |  |  | MINIMUM ZONE TEMPERATURE
| °C |  |  |  | °C |  |  |  | °C
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Tas v9.4.3 | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Tas v9.4.3 | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Tas v9.4.3
| NRCAN | NRCAN | NRCAN |  | NRCAN | NRCAN | NRCAN |  | NRCAN | NRCAN | NRCAN
CASE HE210 | 20.01 | 20 | 19.96 | 20.0456 | 21.45 | 20 | 20.05 | 20.0816 | 20 | 20 | 19.83 | 20.008
CASE HE220 | 18.75 | 18.53 | 18.5 | 18.59 | 22.7 | 20 | 20.05 | 20.0832 | 15 | 15 | 14.88 | 15.0182
CASE HE230 | 15.48 | 15.17 | 15.46 | 15.4392 | 20.14 | 20 | 20.05 | 20.0925 | 1.45 | 4.48 | 5.33 | 1.0338

## YD
RESULTS5-4.XLS
Tas v9.4.3
Output spreadsheet for FURNACE BESTEST
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.76
CASE HE110 | 77.76
CASE HE120 | 31.3586
CASE HE130 | 0.188
CASE HE140 | 31.3582
CASE HE150 | 29.8839
CASE HE160 | 30.731
CASE HE170 | 29.8839
CASE HE210 | 42.3233
CASE HE220 | 40.0693
CASE HE230 | 34.706
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.756
CASE HE110 | 97.4372
CASE HE120 | 38.6062
CASE HE130 | 0.98814
CASE HE140 | 39.2234
CASE HE150 | 37.3059
CASE HE160 | 38.4278
CASE HE170 | 37.3059
CASE HE210 | 52.7689
CASE HE220 | 49.8753
CASE HE230 | 43.4582
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.00026314
CASE HE110 | 0.00032975
CASE HE120 | 0.00013065
CASE HE130 | 3.3441e-06
CASE HE140 | 0.00013274
CASE HE150 | 0.00012625
CASE HE160 | 0.00013005
CASE HE170 | 0.00012625
CASE HE210 | 0.00017858
CASE HE220 | 0.00016879
CASE HE230 | 0.00014707
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 431.9998
CASE HE160 | 174.724
CASE HE170 | 473.626
CASE HE210 | 294.2564
CASE HE220 | 281.8893
CASE HE230 | 482.9875
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.0456
CASE HE220 | 18.59
CASE HE230 | 15.4392
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.0816
CASE HE220 | 20.0832
CASE HE230 | 20.0925
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.008
CASE HE220 | 15.0182
CASE HE230 | 1.0338

## B
Output spreadsheet for Furnace BESTEST
ESP-r /HOT3000 by NRCAN
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.94
CASE HE110 | 77.94
CASE HE120 | 31.25
CASE HE130 | 0
CASE HE140 | 31.26
CASE HE150 | 29.88
CASE HE160 | 31.26
CASE HE170 | 29.88
CASE HE210 | 41.36
CASE HE220 | 39.41
CASE HE230 | 34.32
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.74
CASE HE110 | 96.9201
CASE HE120 | 38.4134
CASE HE130 | 0
CASE HE140 | 39.0044
CASE HE150 | 37.2315
CASE HE160 | 38.118
CASE HE170 | 37.2315
CASE HE210 | 50.5284
CASE HE220 | 47.8691
CASE HE230 | 41.3683
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000263
CASE HE110 | 0.000328
CASE HE120 | 0.00013
CASE HE130 | 0
CASE HE140 | 0.000132
CASE HE150 | 0.000126
CASE HE160 | 0.000129
CASE HE170 | 0.000126
CASE HE210 | 0.000171
CASE HE220 | 0.000162
CASE HE230 | 0.00014
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 432
CASE HE160 | 170.2
CASE HE170 | 473.4
CASE HE210 | 281.6
CASE HE220 | 268.3
CASE HE230 | 458.3
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.01
CASE HE220 | 18.75
CASE HE230 | 15.48
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 21.45
CASE HE220 | 22.7
CASE HE230 | 20.14
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 15
CASE HE230 | 1.45

## C
Output spreadsheet for Furnace BESTEST
EnergyPlus by NRCAN
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.75
CASE HE110 | 77.75
CASE HE120 | 31.1
CASE HE130 | 0
CASE HE140 | 31.1
CASE HE150 | 29.59
CASE HE160 | 30.46
CASE HE170 | 29.59
CASE HE210 | 42.04
CASE HE220 | 39.87
CASE HE230 | 34.59
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.7133
CASE HE110 | 97.2156
CASE HE120 | 38.2657
CASE HE130 | 0
CASE HE140 | 39.0044
CASE HE150 | 36.936
CASE HE160 | 38.118
CASE HE170 | 36.936
CASE HE210 | 52.0059
CASE HE220 | 49.3465
CASE HE230 | 42.5503
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000263
CASE HE110 | 0.000329
CASE HE120 | 0.0001295
CASE HE130 | 0
CASE HE140 | 0.000132
CASE HE150 | 0.000125
CASE HE160 | 0.000129
CASE HE170 | 0.000125
CASE HE210 | 0.000176
CASE HE220 | 0.000167
CASE HE230 | 0.000144
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 433.3
CASE HE160 | 172.2
CASE HE170 | 473.1
CASE HE210 | 291.4
CASE HE220 | 276.1
CASE HE230 | 431.4
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 18.53
CASE HE230 | 15.17
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 20
CASE HE230 | 20
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 15
CASE HE230 | 4.48

## D
Output spreadsheet for Furnace BESTEST
DOE-2.1E by NRCAN
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.73
CASE HE110 | 77.73
CASE HE120 | 31.12
CASE HE130 | 0.15804
CASE HE140 | 31.07
CASE HE150 | 29.55
CASE HE160 | 30.48
CASE HE170 | 29.55
CASE HE210 | 42.08
CASE HE220 | 39.87
CASE HE230 | 34.49
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 78.3043
CASE HE110 | 97.8065
CASE HE120 | 38.4134
CASE HE130 | 0.14479
CASE HE140 | 38.7089
CASE HE150 | 36.6405
CASE HE160 | 37.8225
CASE HE170 | 36.6405
CASE HE210 | 52.3014
CASE HE220 | 49.3465
CASE HE230 | 43.1412
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000265
CASE HE110 | 0.000331
CASE HE120 | 0.00013
CASE HE130 | 4.9e-07
CASE HE140 | 0.000131
CASE HE150 | 0.000124
CASE HE160 | 0.000128
CASE HE170 | 0.000124
CASE HE210 | 0.000177
CASE HE220 | 0.000167
CASE HE230 | 0.000146
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 432.1
CASE HE160 | 172.3
CASE HE170 | 473.3
CASE HE210 | 299.2
CASE HE220 | 282.2
CASE HE230 | 480
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.96
CASE HE220 | 18.5
CASE HE230 | 15.46
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.05
CASE HE220 | 20.05
CASE HE230 | 20.05
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.83
CASE HE220 | 14.88
CASE HE230 | 5.33

## Q
RESULTS.XLS5-4, Jan 27, 2005 |  |  | SEE SHEET 'A' FOR INSTRUCTIONS
NB: (Max-Min)/Analytical is replaced with (Max-Min)/Average for cases 2A,2B and 2C
TOTAL FURNACE LOAD |  | GJ
|  |  |  | Statistics, All Results |  |  | Analytical/semi-analytical
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Heat transfer surf | Infiltration | Tas v9.4.3
|  |  |  | Min | Max | /Analytical | method | method
CASE HE100 | 77.94 | 77.75 | 77.73 | 77.73 | 77.94 | 0.2701% | 77.74 | 77.77 | 77.76
CASE HE110 | 77.94 | 77.75 | 77.73 | 77.73 | 77.94 | 0.2701% | 77.74 | 77.77 | 77.76
CASE HE120 | 31.25 | 31.1 | 31.12 | 31.1 | 31.25 | 0.4823% | 31.1 | 31.11 | 31.3586
CASE HE130 | 0 | 0 | 0.15804 | 0 | 0.15804 | 0% | 0 | 0 | 0.188
CASE HE140 | 31.26 | 31.1 | 31.07 | 31.07 | 31.26 | 0.6109% | 31.1 | 31.11 | 31.3582
CASE HE150 | 29.88 | 29.59 | 29.55 | 29.55 | 29.88 | 1.113% | 29.65 | 29.66 | 29.8839
CASE HE160 | 31.26 | 30.46 | 30.48 | 30.46 | 31.26 | 2.572% | 31.1 | 31.11 | 30.731
CASE HE170 | 29.88 | 29.59 | 29.55 | 29.55 | 29.88 | 1.113% | 29.65 | 29.66 | 29.8839
CASE HE210 | 41.36 | 42.04 | 42.08 | 41.36 | 42.08 | 1.726% | - | - | 42.3233
CASE HE220 | 39.41 | 39.87 | 39.87 | 39.41 | 39.87 | 1.16% | - | - | 40.0693
CASE HE230 | 34.32 | 34.59 | 34.49 | 34.32 | 34.59 | 0.7836% | - | - | 34.706
TOTAL FURNACE INPUT |  | GJ
|  |  |  | Statistics, All Results |  |  | Analytical/semi-analytical
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Heat transfer surf | Infiltration | Tas v9.4.3
|  |  |  | Min | Max | /Analytical | method | method
CASE HE100 | 77.74 | 77.7133 | 78.3043 | 77.7133 | 78.3043 | 0.7605% | 77.7133 | 77.7133 | 77.756
CASE HE110 | 96.9201 | 97.2156 | 97.8065 | 96.9201 | 97.8065 | 0.9119% | 97.2156 | 97.2156 | 97.4372
CASE HE120 | 38.4134 | 38.2657 | 38.4134 | 38.2657 | 38.4134 | 0.3861% | 38.2657 | 38.2952 | 38.6062
CASE HE130 | 0 | 0 | 0.14479 | 0 | 0.14479 | 0% | 0 | 0 | 0.98814
CASE HE140 | 39.0044 | 39.0044 | 38.7089 | 38.7089 | 39.0044 | 0.7576% | 39.0044 | 39.0044 | 39.2234
CASE HE150 | 37.2315 | 36.936 | 36.6405 | 36.6405 | 37.2315 | 1.596% | 37.0246 | 37.0246 | 37.3059
CASE HE160 | 38.118 | 38.118 | 37.8225 | 37.8225 | 38.118 | 0.7758% | 38.0884 | 38.118 | 38.4278
CASE HE170 | 37.2315 | 36.936 | 36.6405 | 36.6405 | 37.2315 | 1.596% | 37.0246 | 37.0246 | 37.3059
CASE HE210 | 50.5284 | 52.0059 | 52.3014 | 50.5284 | 52.3014 | 3.448% | - | - | 52.7689
CASE HE220 | 47.8691 | 49.3465 | 49.3465 | 47.8691 | 49.3465 | 3.04% | - | - | 49.8753
CASE HE230 | 41.3683 | 42.5503 | 43.1412 | 41.3683 | 43.1412 | 4.196% | - | - | 43.4582
FUEL CONSUMPTION |  | m3/s
|  |  |  | Statistics, All Results |  |  | Analytical/semi-analytical
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Heat transfer surf | Infiltration | Tas v9.4.3
|  |  |  | Min | Max | /Analytical | method | method
CASE HE100 | 0.000263 | 0.000263 | 0.000265 | 0.000263 | 0.000265 | 0.7605% | 0.000263 | 0.000263 | 0.00026314
CASE HE110 | 0.000328 | 0.000329 | 0.000331 | 0.000328 | 0.000331 | 0.9119% | 0.000329 | 0.000329 | 0.00032975
CASE HE120 | 0.00013 | 0.0001295 | 0.00013 | 0.0001295 | 0.00013 | 0.3861% | 0.0001295 | 0.0001296 | 0.00013065
CASE HE130 | 0 | 0 | 4.9e-07 | 0 | 4.9e-07 | 0% | 0 | 0 | 3.3441e-06
CASE HE140 | 0.000132 | 0.000132 | 0.000131 | 0.000131 | 0.000132 | 0.7576% | 0.000132 | 0.000132 | 0.00013274
CASE HE150 | 0.000126 | 0.000125 | 0.000124 | 0.000124 | 0.000126 | 1.596% | 0.0001253 | 0.0001253 | 0.00012625
CASE HE160 | 0.000129 | 0.000129 | 0.000128 | 0.000128 | 0.000129 | 0.7758% | 0.0001289 | 0.000129 | 0.00013005
CASE HE170 | 0.000126 | 0.000125 | 0.000124 | 0.000124 | 0.000126 | 1.596% | 0.0001253 | 0.0001253 | 0.00012625
CASE HE210 | 0.000171 | 0.000176 | 0.000177 | 0.000171 | 0.000177 | 3.448% | - | - | 0.00017858
CASE HE220 | 0.000162 | 0.000167 | 0.000167 | 0.000162 | 0.000167 | 3.04% | - | - | 0.00016879
CASE HE230 | 0.00014 | 0.000144 | 0.000146 | 0.00014 | 0.000146 | 4.196% | - | - | 0.00014707
FAN ENERGY (BOTH FANS) |  | Kwh
|  |  |  | Statistics, All Results |  |  | Analytical
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | /semi-analytical | Tas v9.4.3
|  |  |  | Min | Max | /Analytical
CASE HE150 | 432 | 433.3 | 432.1 | 432 | 433.3 | 0.3009% | 432 | 431.9998
CASE HE160 | 170.2 | 172.2 | 172.3 | 170.2 | 172.3 | 1.216% | 172.76 | 174.724
CASE HE170 | 473.4 | 473.1 | 473.3 | 473.1 | 473.4 | 0.0634% | 473.18 | 473.626
CASE HE210 | 281.6 | 291.4 | 299.2 | 281.6 | 299.2 | 6.061% | - | 294.2564
CASE HE220 | 268.3 | 276.1 | 282.2 | 268.3 | 282.2 | 5.05% | - | 281.8893
CASE HE230 | 458.3 | 431.4 | 480 | 431.4 | 480 | 10.66% | - | 482.9875
MEAN ZONE TEMPERATURE |  | °C
Statistics, All Results
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Tas v9.4.3
|  |  |  | Min | Max | /Average
CASE HE210 | 20.01 | 20 | 19.96 | 19.96 | 20.01 | 0.2502% | 20.0456
CASE HE220 | 18.75 | 18.53 | 18.5 | 18.5 | 18.75 | 1.342% | 18.59
CASE HE230 | 15.48 | 15.17 | 15.46 | 15.17 | 15.48 | 2.023% | 15.4392
MAXIMUM ZONE TEMPERATURE |  | °C
Statistics, All Results
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Tas v9.4.3
|  |  |  | Min | Max | /Average
CASE HE210 | 21.45 | 20 | 20.05 | 20 | 21.45 | 6.996% | 20.0816
CASE HE220 | 22.7 | 20 | 20.05 | 20 | 22.7 | 12.65% | 20.0832
CASE HE230 | 20.14 | 20 | 20.05 | 20 | 20.14 | 0.6976% | 20.0925
MINIMUM ZONE TEMPERATURE |  | °C
Statistics, All Results
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Tas v9.4.3
|  |  |  | Min | Max | /Average
CASE HE210 | 20 | 20 | 19.83 | 19.83 | 20 | 0.8536% | 20.008
CASE HE220 | 15 | 15 | 14.88 | 14.88 | 15 | 0.8032% | 15.0182
CASE HE230 | 1.45 | 4.48 | 5.33 | 1.45 | 5.33 | 114.5% | 1.0338